## Sheet1
ANNUAL LOADS					LOW MASS QUALIFICATION TESTS
ANNUAL HEATING [MWH]					ANNUAL HEATING [MWH]					Annual incident solar radiation / kWh/m^2
	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo
CASE	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					Absolute	Sensitivity	All	比率	比率	比率
600	4.296	4.773	5.709	5.226	5.596	4.882	4.872	5.362	4.740	4.296	5.709	5.090	○	-		610-600	0.059	0.033	0.077	0.054	0.024	0.089	0.098	0.021	0.035	0.021	0.098	0.057	○	-		Pass	151	127	278	97.4%	80.9%	89.1%
610	4.355	4.806	5.786	5.280	5.620	4.971	4.970	5.383	4.775	4.355	5.786	5.146	○	-		620-600	0.317	0.276	0.235	0.328	0.138	0.682	0.201	0.366	0.225	0.138	0.682	0.318	○	-		Fail	4	30	34	2.6%	19.1%	10.9%					NORTH	427	0	434	456	407	457	367	453	455
620	4.613	5.049	5.944	5.554	5.734	5.564	5.073	5.728	4.965	4.613	5.944	5.407	○	-		630-620	0.437	0.310	0.525	0.329	0.267	0.531	0.551	1.290	0.403	0.267	0.551	0.530	○	-		未対応	0	0	0	0.0%	0.0%	0.0%					EAST	959	0	1155	1083	1217	1082	1101	962	1080
630	5.050	5.359	6.469	5.883	6.001	6.095	5.624	7.018	5.367	5.050	6.469	5.937	○	-		640-600	-1.545	-1.885	-2.166	-1.971	-1.793	-1.817	-1.829	-2.053	-1.812	-2.166	-1.545	-1.882	○	-					WEST	1086	0	1079	1003	857	1002	1012	1090	1004
640	2.751	2.888	3.543	3.255	3.803	3.065	3.043	3.309	2.928	2.751	3.803	3.207	○	-		ANNUAL COOLING [MWH]					SOUTH	1456	0	1566	1476	1468	1474	1522	1468	1478
650	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000					ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					HORIZONTAL	1797	0	1831	1832	1832	1832	1832	1832	1833
900	1.170	1.610	1.872	1.897	1.988	1.730	1.655	2.041	1.545	1.170	2.041	1.745	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
910	1.575	1.862	2.254	2.174	2.282	2.063	2.097	2.220	1.769	1.575	2.282	2.066	○	-		610-600	-2.222	-1.582	-2.227	-1.830	-2.186	-1.728	-1.891	-1.272	-1.478	-2.227	-1.272	-1.867	○	-
920	3.313	3.752	4.255	4.093	4.058	4.235	3.776	4.300	3.573	3.313	4.300	3.973	○	-		620-600	-2.720	-2.341	-2.745	-2.645	-2.960	-2.481	-2.591	-2.427	-2.155	-2.960	-2.341	-2.614	×	30.1%
930	4.143	4.347	5.335	4.755	4.728	5.168	4.740	6.306	4.373	4.143	5.335	4.940	○	-		630-620	-1.288	-0.984	-1.845	-1.140	-1.303	-1.522	-1.485	-2.630	-1.553	-1.845	-0.984	-1.525	○	-
940	0.793	1.021	1.239	1.231	1.411	1.179	1.080	1.323	1.026	0.793	1.411	1.160	○	-		640-600	-0.185	-0.250	-0.320	-0.252	-0.153	-0.245	-0.246	-0.270	-0.286	-0.320	-0.153	-0.240	○	-
950	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000					650-600	-1.321	-1.293	-1.284	-1.384	-1.419	-1.404	-1.373	-1.322	-1.424	-1.419	-1.284	-1.350	×	-4.0%					Annual transmitted solrad unshaded / kWh/m^2
960	2.311	2.664	2.928	2.884	2.851	2.943	3.373	2.816	2.590	2.311	3.373	2.846	○	-		PEAK HEATING [KW]
990	2.222	3.448	3.425	2.972	4.324	4.301		3.813	3.701	2.222	4.324	3.501	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
195	4.167	4.895	5.871	5.324	4.968	4.973	4.871	4.921	4.966	4.167	5.871	4.999	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
200	5.252	6.559			6.683	6.636	6.395	6.882	6.747	5.252	6.882	6.401	○	-		610-600	0.000	0.001	-0.011	0.000	-0.001	0.000	-0.008	0.000	0.000	-0.011	0.000	-0.002	×	0.3%					WEST	732	0	735	689	563	642	662	706	731
210	6.456	6.559			6.794	6.735	6.554	6.967	7.640	6.456	6.967	6.678	×	131.6%		620-600	0.154	0.001	0.001	0.019	-0.001	0.240	-0.008	0.025	0.006	-0.008	0.240	0.054	○	-					SOUTH	946	0	1051	962	954	926	984	914	974
215	5.547	7.215			7.943	7.281	7.130	7.319	7.484	5.547	7.943	7.073	○	-		630-620	0.001	0.000	-0.021	0.003	0.000	0.001	0.000	0.000	0.001	-0.021	0.003	-0.002	○	-
220	6.944	7.215	8.787	8.102	8.127	7.422	7.297	7.437	8.502	6.944	8.787	7.666	○	-		640-600	1.795	1.546	1.898	2.272	3.771	2.310	1.792	2.600	2.084	1.546	2.600	2.248	○	-
230	10.376	10.740	12.243	11.633	11.649	11.037	10.840	10.964	10.951	10.376	12.243	11.185	○	-		PEAK COOLING [KW]
240	5.649	6.009	7.448	6.769	6.786	6.194	6.076	6.234	7.184	5.649	7.448	6.396	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
250	4.751	5.739	7.024	6.608	6.653	5.974	5.764	5.738	6.746	4.751	7.024	6.031	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
270	4.510	4.930		5.482	5.920	5.072	5.047	5.489	5.423	4.510	5.920	5.207	○	-		610-600	-0.525	-0.141	-0.592	-0.456	-0.336	-0.116	-0.811	-0.666	-0.227	-0.811	-0.116	-0.455	○	-
280	4.675	5.125		5.937	6.148	5.363	5.279	5.841	5.742	4.675	6.148	5.481	○	-		620-600	-2.560	-1.890	-2.226	-2.234	-2.592	-1.989	-2.211	-1.716	-2.109	-2.560	-1.716	-2.177	○	-
290	4.577	4.959		5.539	5.942	5.160	5.132	5.509	5.463	4.577	5.942	5.260	○	-		630-620	-0.562	-0.371	-0.842	-0.477	-0.559	-0.632	-0.667	-1.550	-0.954	-0.842	-0.371	-0.707	×	-23.8%
300	4.761	5.077		5.689	5.964	5.662	5.124	5.786	5.585	4.761	5.964	5.438	○	-		640-600	-0.033	-0.073	-0.080	-0.051	-0.014	-0.036	-0.044	-0.041	-0.059	-0.080	-0.014	-0.047	○	-					Annual transmitted solrad shaded / kWh/m^2
310	5.221	5.327		5.937	6.165	6.154	5.610	7.135	5.967	5.221	7.135	5.936	○	-		650-600	-0.163	-0.134	-0.140	-0.156	-0.093	-0.143	-0.108	-0.133	-0.165	-0.163	-0.108	-0.134	×	-2.8%
320	3.859	4.209		4.764	5.141	4.343	4.348	4.840	4.655	3.859	5.141	4.501	○	-					WEST	599	0	481	554	441	431	438	469	521
395	4.984	4.799	5.835	5.199	5.201	4.967	4.855	4.839	5.401	4.799	5.835	5.085	○	-		HIGH MASS QUALIFICATION TESTS					SOUTH	785	0	831	803	775	757	782	809	829
400	6.900	7.075	8.770	7.966	7.973	7.287	7.166	7.326	8.381	6.900	8.770	7.558	○	-		ANNUAL HEATING [MWH]
410	8.596	8.873	10.506	9.726	9.734	9.019	8.936	9.085	9.599	8.596	10.506	9.309	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
420	7.298	7.610	9.151	8.365	8.373	7.774	7.697	7.863	8.266	7.298	9.151	8.016	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
430	5.429	6.488	7.827	7.178	7.186	6.662	6.500	6.510	6.923	5.429	7.827	6.723	○	-		900-600	-3.126	-3.163	-3.837	-3.329	-3.608	-3.152	-3.217	-3.321	-3.195	-3.837	-3.126	-3.344	○	-
440	4.449	4.987		5.652	5.811	5.152	5.098	5.642	5.012	4.449	5.811	5.256	○	-		910-900	0.405	0.252	0.382	0.277	0.294	0.333	0.442	0.179	0.224	0.179	0.442	0.321	○	-
800	4.868	5.953	7.228	6.611	6.600	6.161	5.940	5.861	6.365	4.868	7.228	6.153	○	-		920-900	2.143	2.142	2.383	2.196	2.070	2.505	2.121	2.259	2.028	2.070	2.505	2.227	×	-9.7%
810	1.839	2.446		3.004	2.828	2.722	2.567	2.962	2.390	1.839	3.004	2.624	○	-		930-920	0.830	0.595	1.080	0.662	0.670	0.933	0.964	2.006	0.800	0.595	1.080	0.968	○	-
ANNUAL COOLING [MWH]					940-900	-0.377	-0.589	-0.633	-0.666	-0.577	-0.551	-0.575	-0.718	-0.519	-0.718	-0.377	-0.586	○	-
	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate		960-900	1.141	1.054	1.056	0.987	0.863	1.213	1.718	0.775	1.045	0.775	1.718	1.101	○	-
CASE#	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					990-900	1.052	1.838	1.553	1.075	2.336	2.571		1.772	2.156	1.052	2.571	1.742	○	-
600	6.137	6.433	7.079	7.278	7.964	6.492	6.492	6.778	6.411	6.137	7.964	6.832	○	-		ANNUAL COOLING [MWH]
610	3.915	4.851	4.852	5.448	5.778	4.764	4.601	5.506	4.934	3.915	5.778	4.964	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					395	4.98	4.8	5.84	5.2	5.2	4.97	4.86	4.84	5.401	Low mass annual heating / MWh
620	3.417	4.092	4.334	4.633	5.004	4.011	3.901	4.351	4.257	3.417	5.004	4.218	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					430	5.43	6.49	7.83	7.18	7.19	6.66	6.5	6.51	6.923
630	2.129	3.108	2.489	3.493	3.701	2.489	2.416	1.721	2.703	2.129	3.701	2.693	○	-		900-600	-4.005	-3.833	-4.624	-4.113	-4.549	-3.920	-4.007	-4.179	-3.981	-4.624	-3.833	-4.154	○	-					600	4.3	4.77	5.71	5.23	5.6	4.88	4.87	5.36	4.740
640	5.952	6.183	6.759	7.026	7.811	6.247	6.246	6.508	6.126	5.952	7.811	6.592	○	-		910-900	-1.311	-1.067	-1.479	-1.293	-1.561	-1.144	-1.159	-0.832	-1.006	-1.561	-0.832	-1.231	○	-					610	4.36	4.81	5.79	5.28	5.62	4.97	4.97	5.38	4.775
650	4.816	5.140	5.795	5.894	6.545	5.088	5.119	5.456	4.987	4.816	6.545	5.482	○	-		920-900	-0.292	0.016	-0.015	-0.222	-0.323	-0.115	-0.067	0.014	0.204	-0.323	0.016	-0.126	×	55.4%					620	4.61	5.05	5.94	5.55	5.73	5.56	5.07	5.73	4.965
900	2.132	2.600	2.455	3.165	3.415	2.572	2.485	2.599	2.431	2.132	3.415	2.678	○	-		930-920	-0.801	-0.682	-1.174	-0.770	-0.854	-1.018	-1.002	-1.719	-1.075	-1.174	-0.682	-1.003	○	-					630	5.05	5.36	6.47	5.88	6	6.1	5.62	7.02	5.367
910	0.821	1.533	0.976	1.872	1.854	1.428	1.326	1.767	1.425	0.821	1.872	1.447	○	-		940-900	-0.053	-0.064	-0.115	-0.129	-0.174	-0.083	-0.102	-0.083	-0.098	-0.174	-0.053	-0.100	○	-					640	2.75	2.89	3.54	3.26	3.8	3.07	3.04	3.31	2.928
920	1.840	2.616	2.440	2.943	3.092	2.457	2.418	2.613	2.634	1.840	3.092	2.552	○	-		950-900	-1.745	-2.074	-1.917	-2.244	-2.826	-2.021	-1.924	-1.828	-1.909	-2.826	-1.745	-2.072	○	-
930	1.039	1.934	1.266	2.173	2.238	1.439	1.416	0.894	1.560	1.039	2.238	1.550	○	-		960-900	-1.644	-1.934	-2.027	-2.362	-2.697	-1.929	-2.074	-1.813	-1.900	-2.697	-1.644	-2.060	○	-
940	2.079	2.536	2.340	3.036	3.241	2.489	2.383	2.516	2.332	2.079	3.241	2.578	○	-		990-900	-1.131	-0.960	-0.614	-1.778	-2.701	-1.956		-1.211	-1.795	-2.701	-0.614	-1.479	○	-
950	0.387	0.526	0.538	0.921	0.589	0.551	0.561	0.771	0.522	0.387	0.921	0.605	○	-		PEAK HEATING [KW]
960	0.488	0.666	0.428	0.803	0.718	0.643	0.411	0.786	0.530	0.411	0.803	0.618	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
990	1.001	1.640	1.841	1.387	0.714	0.616		1.388	0.636	0.616	1.841	1.227	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
195	0.414	0.421	0.264	0.510	0.488	0.474	0.474	0.443	0.442	0.264	0.510	0.436	○	-		900-600	-0.587	-0.487	-0.488	-0.498	-0.226	-0.429	-0.414	-0.557	-0.447	-0.587	-0.414	-0.461	○	-					395	0	0.01	0	0.02	0.01	0.01	0.01	0.01	0.000
200	0.570	0.613			0.699	0.677	0.716	0.633	0.668	0.570	0.716	0.651	○	-		910-900	0.008	0.003	0.007	0.004	0.002	0.010	0.019	0.004	0.001	0.003	0.019	0.007	×	-12.5%					430	0.54	0.62	0.42	0.7	0.68	0.56	0.62	0.88	0.801	Low mass annual cooling / MWh
210	0.162	0.613			0.681	0.661	0.668	0.641	0.432	0.162	0.681	0.571	○	-		920-900	0.458	0.250	0.248	0.253	0.075	0.421	0.192	0.264	0.205	0.192	0.458	0.270	○	-					600	6.14	6.43	7.08	7.28	7.96	6.49	6.49	6.78	6.411
215	0.639	0.701			0.853	0.749	0.765	0.671	0.747	0.639	0.853	0.730	○	-		930-920	0.047	0.029	0.027	0.029	0.009	0.035	0.036	0.127	0.027	0.027	0.127	0.042	×	-0.1%					610	3.92	4.85	4.85	5.45	5.78	4.76	4.6	5.51	4.934
220	0.186	0.701	0.399	0.827	0.835	0.734	0.737	0.683	0.468	0.186	0.835	0.638	○	-		940-900	1.130	1.575	2.108	2.356	5.842	2.509	1.606	2.631	2.324	1.130	2.631	2.470	○	-					620	3.42	4.09	4.33	4.63	5	4.01	3.9	4.35	4.257
230	0.454	0.976	0.692	1.131	1.139	1.020	1.040	0.985	0.673	0.454	1.139	0.930	○	-		960-900	-0.440	-0.702	-0.830	-0.897	-1.185	-0.756	-0.995	-1.018	-0.741	-1.018	-0.440	-0.853	○	-					630	2.13	3.11	2.49	3.49	3.7	2.49	2.42	1.72	2.703
240	0.415	1.072	0.660	1.239	1.246	1.108	1.114	1.045	0.752	0.415	1.246	0.987	○	-		990-900	-0.081	0.281	-0.130	-0.079	-0.343	0.191		0.499	-0.282	-0.343	0.499	0.048	○	-					650	4.82	5.14	5.8	5.89	6.55	5.09	5.12	5.46	4.987
250	3.213	2.545	2.177	2.924	2.931	2.486	2.684	3.380	3.132	2.177	3.380	2.793	○	-		PEAK COOLING [KW]
270	7.528	8.670		9.631	10.350	8.795	8.764	8.714	8.544	7.528	10.350	8.922	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
280	4.873	5.895		6.511	7.114	5.805	5.761	6.257	5.643	4.873	7.114	6.031	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
290	5.204	7.011		7.721	8.089	6.903	6.699	7.431	6.945	5.204	8.089	7.008	○	-		900-600	-3.306	-2.810	-3.198	-2.956	-2.650	-2.952	-2.919	-3.355	-2.886	-3.355	-2.810	-3.018	○	-
300	4.302	5.836		6.525	7.100	5.849	5.721	5.781	5.664	4.302	7.100	5.873	○	-		910-900	-0.992	-0.655	-1.122	-0.594	-0.928	-0.548	-0.775	-0.310	-0.541	-1.122	-0.310	-0.741	○	-
310	2.732	4.570		5.136	5.471	3.875	3.727	2.471	3.799	2.471	5.471	3.997	○	-		920-900	-0.503	-0.222	-0.349	-0.384	-1.124	-0.263	-0.517	0.048	-0.292	-0.517	0.048	-0.414	○	-
320	5.061	5.906		6.576	7.304	5.914	5.956	5.663	5.748	5.061	7.304	6.054	○	-		930-920	-0.512	-0.387	-0.721	-0.407	-0.574	-0.585	-0.552	-1.201	-0.760	-0.721	-0.387	-0.617	×	-11.5%					395	2.06	2.21	2.33	2.39	2.39	2.26	2.22	2.27	2.337
395	0.000	0.011	0.000	0.016	0.014	0.010	0.010	0.011	0.000	0.000	0.016	0.009	○	-		940-900	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000					430	3.44	3.94	4.05	4.29	4.3	4.04	3.93	4.14	3.920
400	0.000	0.040	0.002	0.061	0.058	0.042	0.045	0.044	0.004	0.000	0.061	0.036	○	-		950-900	-0.855	-0.534	-0.794	-0.701	-1.053	-0.657	-0.881	-0.590	-0.876	-0.881	-0.534	-0.758	○	-					600	6.19	5.97	6.66	6.83	7.55	6.29	6.49	6.81	6.184
410	0.000	0.059	0.010	0.084	0.084	0.063	0.067	0.065	0.011	0.000	0.084	0.054	○	-		960-900	-1.935	-2.011	-2.401	-2.501	-3.595	-2.155	-2.189	-2.054	-2.234	-2.401	-1.935	-2.355	○	-					610	5.67	5.82	6.06	6.37	7.22	6.17	5.68	6.15	5.957	Low mass peak heating / kW
420	0.011	0.147	0.051	0.189	0.188	0.154	0.158	0.143	0.055	0.011	0.189	0.130	○	-		990-900	-0.466	-0.243	-0.022	-1.052	-1.376	-1.475		-0.678	-1.173	-1.475	-0.022	-0.759	○	-					620	3.63	4.08	4.43	4.59	4.96	4.3	4.28	5.1	4.075
430	0.542	0.617	0.422	0.704	0.684	0.563	0.617	0.875	0.801	0.422	0.875	0.628	○	-					630	3.07	3.7	3.59	4.12	4.4	3.67	3.61	3.55	3.121
440	3.967	4.172		4.674	5.204	3.992	3.975	4.684	4.109	3.967	5.204	4.381	○	-					640	6.16	5.89	6.58	6.78	7.54	6.25	6.44	6.77	6.125
800	0.113	0.224	0.055	0.272	0.222	0.195	0.207	0.325	0.270	0.055	0.325	0.202	○	-		LOW MASS PRIMITIVE DIAGNOSTIC TESTS
810	1.052	1.405		1.711	1.708	1.307	1.191	1.624	1.165	1.052	1.711	1.428	○	-		ANNUAL HEATING [MWH]
				ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS					CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate		200-195	1.085	1.664			1.715	1.663	1.524	1.961	1.781	1.085	1.961	1.602	○	-
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					210-200	1.204	0.000			0.111	0.099	0.159	0.085	0.893	0.000	1.204	0.276	○	-
CASE#	KW	KW	KW	KW	KW	KW	KW	KW	KW	KW	KW					220-215	1.397	0.000			0.184	0.141	0.167	0.118	1.018	0.000	1.397	0.335	○	-					395	0	0.36	0	0.39	0.42	0.36	0.36	0.35	0.117
600	3.437	3.940	4.045	4.258	4.307	4.037	3.931	4.354	3.831	3.437	4.354	4.039	○	-		215-200	0.295	0.656			1.260	0.645	0.735	0.437	0.737	0.295	1.260	0.671	○	-					430	1.49	1.77	1.43	1.76	1.78	1.58	1.8	2.58	1.933
610	3.437	3.941	4.034	4.258	4.306	4.037	3.922	4.354	3.831	3.437	4.354	4.036	○	-		220-210	0.488	0.656			1.333	0.687	0.743	0.470	0.863	0.470	1.333	0.730	○	-					600	6.19	5.97	6.66	6.83	7.55	6.29	6.49	6.81	6.184
620	3.591	3.941	4.046	4.277	4.306	4.277	3.922	4.379	3.837	3.591	4.379	4.092	○	-		230-220	3.432	3.525	3.456	3.531	3.522	3.615	3.543	3.527	2.448	3.432	3.615	3.519	×	-537.5%					610	5.67	5.82	6.06	6.37	7.22	6.17	5.68	6.15	5.957
630	3.592	3.941	4.025	4.280	4.306	4.278	3.922	4.379	3.837	3.592	4.278	4.090	○	-		240-220	-1.295	-1.206	-1.339	-1.333	-1.341	-1.228	-1.221	-1.203	-1.319	-1.341	-1.203	-1.271	○	-					620	3.63	4.08	4.43	4.59	4.96	4.3	4.28	5.1	4.075	Low mass peak cooling / kW
640	5.232	5.486	5.943	6.530	8.078	6.347	5.722	6.954	5.915	5.232	6.954	6.287	○	-		250-220	-2.193	-1.476	-1.763	-1.494	-1.474	-1.448	-1.533	-1.699	-1.757	-2.193	-1.448	-1.635	○	-					630	3.07	3.7	3.59	4.12	4.4	3.67	3.61	3.55	3.121
650	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000					270-220	-2.434	-2.285		-2.620	-2.207	-2.350	-2.250	-1.948	-3.079	-2.620	-1.948	-2.299	×	-68.3%					650	6.03	5.83	6.52	6.67	7.46	6.14	6.38	6.68	6.019
900	2.850	3.453	3.557	3.760	4.081	3.608	3.517	3.797	3.384	2.850	3.797	3.578	○	-		280-270	0.165	0.195		0.455	0.228	0.291	0.232	0.352	0.319	0.165	0.455	0.274	○	-
910	2.858	3.456	3.564	3.764	4.083	3.618	3.536	3.801	3.385	2.858	3.801	3.585	○	-		320-270	-0.651	-0.721		-0.718	-0.779	-0.729	-0.699	-0.649	-0.769	-0.779	-0.649	-0.707	○	-
920	3.308	3.703	3.805	4.013	4.156	4.029	3.708	4.061	3.590	3.308	4.061	3.848	○	-		290-270	0.067	0.029		0.057	0.022	0.088	0.085	0.020	0.039	0.020	0.088	0.053	○	-
930	3.355	3.732	3.832	4.042	4.165	4.064	3.744	4.188	3.617	3.355	4.064	3.890	○	-		300-270	0.251	0.147		0.207	0.044	0.590	0.077	0.297	0.162	0.044	0.590	0.230	○	-
940	3.980	5.028	5.665	6.116	9.923	6.117	5.122	6.428	5.708	3.980	6.428	6.047	○	-		310-300	0.460	0.250		0.248	0.201	0.492	0.486	1.349	0.382	0.201	1.349	0.498	○	-
950	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000					ANNUAL COOLING [MWH]
960	2.410	2.751	2.727	2.863	2.896	2.852	2.522	2.779	2.643	2.410	2.896	2.725	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					600FF	64.93	65.11	69.5	68.6	69.81	64.9	65.25	65.25	65.453
990	2.769	3.734	3.427	3.681	3.738	3.799		4.296	3.103	2.769	4.296	3.635	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					900FF	41.81	43.44	42.7	44.8	43.44	43	42.46	43.17	42.157
195	2.004	2.186	2.320	2.385	2.235	2.221	2.186	2.263	2.209	2.004	2.385	2.225	○	-		200-195	0.156	0.192			0.211	0.203	0.241	0.190	0.226	0.156	0.241	0.199	○	-					650FF	63.24	63.45	68.2	67	68.49	63.3	63.74	63.82	63.569
200	2.651	2.973			3.047	2.999	2.969	3.382	3.035	2.651	3.382	3.004	○	-		210-200	-0.408	0.000			-0.018	-0.016	-0.048	0.008	-0.235	-0.408	0.008	-0.080	○	-					950FF	35.54	36.23	35.9	38.5	35.65	36.1	35.67	37.58	35.563
210	2.701	2.973			3.077	3.020	2.981	3.325	3.212	2.701	3.325	3.013	○	-		220-215	-0.453	0.000			-0.018	-0.015	-0.028	0.012	-0.279	-0.453	0.012	-0.084	○	-					960	48.94	48.88	49	51	51.21	50.2	55.34	48.92	67.555
215	2.787	3.280			3.650	3.307	3.294	3.458	3.373	2.787	3.650	3.296	○	-		215-200	0.069	0.088			0.154	0.072	0.050	0.038	0.079	0.038	0.154	0.078	○	-					Maximum hourly annual temperature / C
220	2.867	3.280	3.465	3.695	3.709	3.348	3.336	3.520	3.562	2.867	3.709	3.403	○	-		220-210	0.024	0.088			0.154	0.073	0.069	0.042	0.036	0.024	0.154	0.075	○	-
230	4.386	4.984	4.994	5.279	5.293	5.159	4.892	5.107	4.643	4.386	5.293	5.012	○	-		230-220	0.268	0.275	0.293	0.304	0.304	0.286	0.303	0.302	0.205	0.268	0.304	0.292	×	-176.3%
240	2.685	3.100	3.282	3.495	3.509	3.159	3.153	3.333	3.379	2.685	3.509	3.214	○	-		240-220	0.229	0.371	0.261	0.412	0.411	0.374	0.377	0.362	0.284	0.229	0.412	0.350	○	-
250	2.866	3.279	3.465	3.695	3.709	3.341	3.336	3.525	3.561	2.866	3.709	3.402	○	-		250-220	3.027	1.844	1.778	2.097	2.096	1.752	1.947	2.697	2.664	1.752	3.027	2.155	○	-
270	2.863	3.277		3.670	3.714	3.340	3.336	3.738	3.476	2.863	3.738	3.420	○	-		270-220	7.342	7.969		8.804	9.515	8.061	8.027	8.031	8.076	7.342	9.515	8.250	○	-
280	2.864	3.278		3.685	3.714	3.341	3.336	3.759	3.478	2.864	3.759	3.425	○	-		280-270	-2.655	-2.775		-3.120	-3.236	-2.990	-3.003	-2.457	-2.901	-3.236	-2.457	-2.891	○	-
290	2.863	3.277		3.670	3.714	3.340	3.328	3.738	3.476	2.863	3.738	3.419	○	-		320-270	-2.467	-2.764		-3.055	-3.046	-2.881	-2.808	-3.051	-2.795	-3.055	-2.467	-2.867	○	-
300	3.014	3.276		3.685	3.714	3.599	3.328	3.770	3.479	3.014	3.770	3.484	○	-		290-270	-2.324	-1.659		-1.910	-2.261	-1.892	-2.065	-1.283	-1.599	-2.324	-1.283	-1.913	○	-					600FF	-15.57	-17.05	-18.8	-18	-9.96	-17.8	-17.81	-18.47	(18.394)
310	3.015	3.277		3.672	3.714	3.599	3.328	3.771	3.480	3.015	3.771	3.482	○	-		300-270	-3.226	-2.834		-3.106	-3.250	-2.946	-3.043	-2.933	-2.879	-3.250	-2.834	-3.048	○	-					900FF	-1.65	-3.15	-4.3	-4.5	-3.94	-4	-6.38	-5.64	(3.944)
320	2.861	3.275		3.661	3.714	3.340	3.336	3.735	3.472	2.861	3.735	3.417	○	-		310-300	-1.570	-1.266		-1.389	-1.629	-1.974	-1.994	-3.310	-1.865	-3.310	-1.266	-1.876	○	-					650FF	-22.56	-22.96	-21.6	-23	-9.97	-22.9	-22.83	-22.91	(23.003)
395	2.062	2.209	2.328	2.385	2.391	2.263	2.221	2.270	2.337	2.062	2.391	2.266	○	-		PEAK HEATING [KW]					950FF	-19.48	-20.04	-18.6	-19.7	-9.83	-20.2	-19.34	-19.96	(18.797)
400	2.867	3.280	3.476	3.695	3.709	3.342	3.336	3.520	3.562	2.867	3.709	3.403	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					960	2.73	1.63	3.9	3.1	2.22	1.4	-2.82	-0.39	(4.115)
410	3.625	4.124	4.233	4.487	4.501	4.227	4.114	4.314	4.103	3.625	4.501	4.203	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
420	3.443	3.944	4.050	4.287	4.301	4.044	3.931	4.126	3.920	3.443	4.301	4.016	○	-		200-195	0.647	0.787			0.812	0.778	0.784	1.119	0.825	0.647	1.119	0.821	○	-					Minimum hourly annual temperature / C
430	3.442	3.944	4.050	4.287	4.301	4.044	3.931	4.137	3.920	3.442	4.301	4.017	○	-		210-200	0.050	0.000			0.030	0.021	0.011	-0.057	0.178	-0.057	0.050	0.009	×	119.2%
440	3.439	3.942		4.277	4.306	4.041	3.931	4.376	3.836	3.439	4.376	4.045	○	-		220-215	0.080	0.000			0.059	0.041	0.042	0.062	0.189	0.000	0.080	0.047	×	135.8%
800	3.227	3.793	3.909	4.138	4.188	3.902	3.786	3.939	3.758	3.227	4.188	3.860	○	-		215-200	0.136	0.307			0.603	0.308	0.325	0.076	0.339	0.076	0.603	0.293	○	-
810	2.979	3.566		3.915	4.115	3.709	3.606	3.963	3.476	2.979	4.115	3.693	○	-		220-210	0.166	0.307			0.632	0.328	0.356	0.195	0.350	0.166	0.632	0.331	○	-
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS					230-220	1.519	1.704	1.529	1.584	1.584	1.811	1.556	1.587	1.082	1.519	1.811	1.609	×	-149.8%
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate		240-220	-0.182	-0.180	-0.183	-0.200	-0.200	-0.189	-0.183	-0.187	-0.183	-0.200	-0.180	-0.188	○	-
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					250-220	-0.001	-0.001	0.000	0.000	0.000	-0.007	0.000	0.005	0.000	-0.007	0.005	-0.001	○	-					600FF	25.13	25.43	24.6	25.48	25.93	25.2	24.49	24.22	25.236
CASE#	KW	KW	KW	KW	KW	KW	KW	KW	KW	KW	KW					270-220	-0.004	-0.003		-0.025	0.005	-0.008	0.000	0.218	-0.086	-0.025	0.218	0.026	×	-25.3%					900FF	25.45	25.93	24.7	25.49	25.72	25.2	24.47	24.45	25.275
600	6.194	5.965	6.656	6.827	7.551	6.286	6.486	6.812	6.184	5.965	6.812	6.597	○	-		280-270	0.001	0.001		0.015	0.000	0.001	0.000	0.021	0.002	0.000	0.021	0.006	○	-					650FF	18.23	18.69	19.1	18.96	19.62	18.4	17.99	18.36	18.732
610	5.669	5.824	6.064	6.371	7.215	6.170	5.675	6.146	5.957	5.669	6.146	6.142	○	-		320-270	-0.002	-0.002		-0.009	0.000	0.000	0.000	-0.003	-0.004	-0.009	0.000	-0.002	○	-					950FF	14.14	14.26	14.3	14.97	14.29	14	14.53	14.64	14.750
620	3.634	4.075	4.430	4.593	4.959	4.297	4.275	5.096	4.075	3.634	5.096	4.420	○	-		290-270	0.000	0.000		0.000	0.000	0.000	-0.008	0.000	0.000	-0.008	0.000	-0.001	×	0.1%					960	27.49	27.72	28	28.69	28.54	28	28.96	26.43	27.905
630	3.072	3.704	3.588	4.116	4.400	3.665	3.608	3.546	3.121	3.072	3.704	3.712	○	-		300-270	0.151	-0.001		0.015	0.000	0.259	-0.008	0.032	0.003	-0.008	0.259	0.064	○	-
640	6.161	5.892	6.576	6.776	7.537	6.250	6.442	6.771	6.125	5.892	7.537	6.551	○	-		310-300	0.001	0.001		-0.013	0.000	0.000	0.000	0.001	0.001	-0.013	0.001	-0.001	○	-
650	6.031	5.831	6.516	6.671	7.458	6.143	6.378	6.679	6.019	5.831	6.679	6.463	○	-		PEAK COOLING [KW]
900	2.888	3.155	3.458	3.871	4.901	3.334	3.567	3.457	3.298	2.888	3.567	3.579	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					Average hourly annual temperature / C
910	1.896	2.500	2.336	3.277	3.973	2.786	2.792	3.147	2.757	1.896	3.147	2.838	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
920	2.385	2.933	3.109	3.487	3.777	3.071	3.050	3.505	3.006	2.385	3.505	3.165	○	-		200-195	0.212	0.289			0.305	0.306	0.309	0.336	0.335	0.212	0.336	0.293	○	-
930	1.873	2.546	2.388	3.080	3.203	2.486	2.498	2.304	2.246	1.873	2.546	2.547	○	-		210-200	-0.387	0.000			-0.010	-0.008	-0.033	0.016	-0.144	-0.387	0.016	-0.070	○	-
940	2.888	3.155	3.458	3.871	4.901	3.334	3.567	3.457	3.298	2.888	4.901	3.579	○	-		220-215	-0.447	0.000			-0.005	-0.001	-0.005	0.021	-0.173	-0.447	0.021	-0.073	○	-
950	2.033	2.621	2.664	3.170	3.848	2.677	2.686	2.867	2.422	2.033	2.867	2.821	○	-		215-200	0.144	0.149			0.236	0.111	0.083	0.066	0.127	0.066	0.236	0.132	○	-					Annual Heating	2.222	3.448	3.425	2.972	4.324	4.301	0.000	3.813	3.701
960	0.953	1.144	1.057	1.370	1.306	1.179	1.378	1.403	1.064	0.953	1.403	1.224	○	-		220-210	0.084	0.149			0.241	0.118	0.111	0.071	0.099	0.071	0.241	0.129	○	-					Annual Cooling	1.001	1.640	1.841	1.387	0.714	0.616	0.000	1.388	0.636
990	2.422	2.912	3.436	2.819	3.525	1.859		2.779	2.124	1.859	3.525	2.822	○	-		230-220	0.499	0.480	0.518	0.535	0.536	0.485	0.529	0.536	0.363	0.480	0.536	0.515	×	-209.4%					Peak Heating	2.422	2.912	3.436	2.819	3.525	1.859	0.000	2.779	2.124
195	0.651	0.728	0.616	0.853	0.806	0.799	0.791	0.790	0.758	0.616	0.853	0.754	○	-		240-220	0.179	0.181	0.182	0.200	0.200	0.183	0.183	0.184	0.183	0.179	0.200	0.186	○	-					Peak Cooling	2.422	2.912	3.436	2.819	3.525	1.859	0.000	2.779	2.124
200	0.863	1.017			1.111	1.105	1.101	1.126	1.093	0.863	1.126	1.054	○	-		250-220	2.800	1.870	1.668	1.250	1.240	1.043	2.049	3.699	1.966	1.043	3.699	1.952	○	-
210	0.476	1.017			1.101	1.097	1.068	1.142	0.949	0.476	1.142	0.983	○	-		270-220	5.796	5.475		5.823	6.625	5.604	5.585	5.654	5.511	5.475	6.625	5.795	○	-
215	1.007	1.166			1.347	1.216	1.184	1.192	1.221	1.007	1.347	1.185	○	-		280-270	-1.912	-2.010		-1.943	-2.208	-2.189	-1.978	-1.631	-1.880	-2.208	-1.631	-1.982	○	-
220	0.560	1.166	0.937	1.340	1.342	1.215	1.179	1.213	1.048	0.560	1.342	1.119	○	-		320-270	-0.655	-0.695		-0.679	-0.635	-0.636	-0.586	-0.726	-0.623	-0.726	-0.586	-0.659	○	-
230	1.059	1.646	1.455	1.875	1.878	1.700	1.708	1.749	1.411	1.059	1.878	1.634	○	-		290-270	-0.087	-0.086		-0.253	-0.174	-0.119	-0.561	-0.246	-0.084	-0.561	-0.086	-0.218	×	0.5%					Ground coupling annual and peak heating and cooling / MWh, kW
240	0.739	1.347	1.119	1.540	1.542	1.398	1.361	1.397	1.231	0.739	1.542	1.305	○	-		300-270	-2.952	-2.548		-2.521	-2.895	-2.483	-2.486	-1.938	-2.509	-2.952	-1.938	-2.546	○	-
250	3.360	3.036	2.605	2.590	2.582	2.258	3.228	4.912	3.014	2.258	4.912	3.071	○	-		310-300	-0.556	-0.344		-0.456	-0.406	-0.667	-0.689	-1.504	-0.956	-1.504	-0.344	-0.660	○	-
270	6.356	6.641		7.163	7.967	6.819	6.764	6.867	6.559	6.356	7.967	6.940	○	-
280	4.444	4.631		5.220	5.759	4.630	4.786	5.236	4.679	4.444	5.759	4.958	○	-		LOW MASS REALISTIC DIAGNOSTIC TESTS
290	6.269	6.555		6.910	7.793	6.700	6.203	6.621	6.476	6.203	7.793	6.722	○	-		ANNUAL HEATING [MWH]					195	4.17	4.9	5.87	5.32	4.97	4.97	4.87	4.92	4.966
300	3.404	4.093		4.642	5.072	4.336	4.278	4.929	4.051	3.404	5.072	4.393	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					200	5.25	6.56	0	0	6.68	6.64	6.4	6.88	6.747
310	2.848	3.749		4.186	4.666	3.669	3.589	3.425	3.095	2.848	4.666	3.733	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					210	6.46	6.56	0	0	6.79	6.74	6.55	6.97	7.640
320	5.701	5.946		6.484	7.332	6.183	6.178	6.141	5.936	5.701	7.332	6.281	○	-		400-395	1.916	2.276	2.935	2.767	2.772	2.320	2.311	2.487	2.980	1.916	2.935	2.473	×	4.4%					215	5.55	7.22	0	0	7.94	7.28	7.13	7.32	7.484
395	0.000	0.362	0.000	0.394	0.421	0.356	0.363	0.345	0.117	0.000	0.421	0.280	○	-		410-400	1.696	1.798	1.736	1.760	1.761	1.732	1.770	1.759	1.218	1.696	1.798	1.752	×	-468.3%					220	6.94	7.22	8.79	8.1	8.13	7.42	7.3	7.44	8.502
400	0.000	0.581	0.265	0.666	0.712	0.612	0.613	0.572	0.375	0.000	0.712	0.503	○	-		420-410	-1.298	-1.263	-1.355	-1.361	-1.361	-1.245	-1.239	-1.222	-1.333	-1.361	-1.222	-1.293	○	-					230	10.38	10.74	12.24	11.63	11.65	11.04	10.84	10.96	10.951
410	0.035	0.699	0.413	0.814	0.863	0.724	0.743	0.710	0.484	0.035	0.863	0.625	○	-		430-420	-1.869	-1.122	-1.324	-1.187	-1.187	-1.112	-1.197	-1.353	-1.343	-1.869	-1.112	-1.294	○	-					240	5.65	6.01	7.45	6.77	6.79	6.19	6.08	6.23	7.184
420	0.258	0.923	0.631	1.047	1.078	0.938	0.938	0.921	0.718	0.258	1.078	0.842	○	-		600-430	-1.133	-1.715	-2.118	-1.952	-1.590	-1.780	-1.628	-1.148	-2.183	-2.118	-1.133	-1.633	×	-6.6%
430	1.493	1.772	1.427	1.762	1.779	1.575	1.798	2.578	1.933	1.427	2.578	1.773	○	-		440-600	0.153	0.214		0.426	0.215	0.270	0.226	0.280	0.272	0.153	0.426	0.255	○	-
440	4.546	4.424		5.053	5.615	4.465	4.686	5.278	4.579	4.424	5.615	4.867	○	-		ANNUAL COOLING [MWH]
800	0.585	0.967	0.743	1.352	1.382	1.028	0.983	1.358	1.284	0.585	1.382	1.050	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					Low mass annual heating (A) / MWh
810	1.852	2.357		2.991	3.624	2.432	2.344	2.862	2.231	1.852	3.624	2.637	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
FREE-FLOAT TEMPERATURE OUTPUT					400-395	0.000	0.029	0.002	0.045	0.044	0.032	0.034	0.033	0.004	0.000	0.045	0.027	○	-
MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)					410-400	0.000	0.019	0.008	0.023	0.026	0.021	0.022	0.021	0.007	0.000	0.026	0.018	○	-					195	0.4	0.4	0.3	0.5	0.5	0.5	0.5	0.4	0.4
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate		420-410	0.011	0.088	0.041	0.105	0.104	0.091	0.090	0.078	0.044	0.011	0.105	0.076	○	-					200	0.6	0.6	0.0	0.0	0.7	0.7	0.7	0.6	0.7
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					430-420	0.531	0.470	0.371	0.515	0.496	0.409	0.460	0.732	0.746	0.371	0.732	0.498	×	4.0%					210	0.2	0.6	0.0	0.0	0.7	0.7	0.7	0.6	0.4
CASE#	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)					600-430	5.595	5.816	6.657	6.574	7.280	5.929	5.875	5.903	5.610	5.595	7.280	6.204	○	-					215	0.6	0.7	0.0	0.0	0.9	0.7	0.8	0.7	0.7
600FF	64.9	65.1	69.5	68.6	69.8	64.9	65.3	65.3	65.5	64.900	69.810	66.669	○	-		440-600	-2.170	-2.261		-2.604	-2.760	-2.500	-2.517	-2.094	-2.302	-2.760	-2.094	-2.415	○	-					220	0.2	0.7	0.4	0.8	0.8	0.7	0.7	0.7	0.5
900FF	41.8	43.4	42.7	44.8	43.4	43.0	42.5	43.2	42.2	41.812	44.800	43.103	○	-		PEAK HEATING [KW]					230	0.5	1.0	0.7	1.1	1.1	1.0	1.0	1.0	0.7
650FF	63.2	63.5	68.2	67.0	68.5	63.3	63.7	63.8	63.6	63.236	68.490	65.155	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					240	0.4	1.1	0.7	1.2	1.2	1.1	1.1	1.0	0.8
950FF	35.5	36.2	35.9	38.5	35.7	36.1	35.7	37.6	35.6	35.540	38.500	36.396	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
960	48.9	48.9	49.0	51.0	51.2	50.2	55.3	48.9	67.6	48.880	55.340	50.437	×	189.1%		400-395	0.805	1.071	1.148	1.310	1.318	1.079	1.115	1.250	1.225	0.805	1.318	1.137	○	-
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)					410-400	0.758	0.844	0.757	0.792	0.792	0.885	0.778	0.794	0.541	0.757	0.885	0.800	×	-168.9%
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate		420-410	-0.182	-0.180	-0.183	-0.200	-0.200	-0.183	-0.183	-0.188	-0.183	-0.200	-0.180	-0.187	○	-
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					430-420	-0.001	0.000	0.000	0.000	0.000	0.000	0.000	0.011	0.000	-0.001	0.011	0.001	○	-					Low mass annual cooling (A) / MWh
CASE#	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)					600-430	-0.005	-0.004	-0.005	-0.029	0.006	-0.007	0.000	0.217	-0.089	-0.029	0.217	0.022	×	-24.3%
600FF	-15.6	-17.1	-18.8	-18.0	-10.0	-17.8	-17.8	-18.5	-18.4	-18.800	-9.960	-16.682	○	-		440-600	0.002	0.002		0.019	-0.001	0.004	0.000	0.022	0.005	-0.001	0.022	0.007	○	-					195	2	2.19	2.32	2.39	2.24	2.22	2.19	2.26	2.209
900FF	-1.6	-3.2	-4.3	-4.5	-3.9	-4.0	-6.4	-5.6	-3.9	-6.380	-1.647	-4.195	○	-		PEAK COOLING [KW]					200	2.65	2.97	0	0	3.05	3	2.97	3.38	3.035
650FF	-22.6	-23.0	-21.6	-23.0	-10.0	-22.9	-22.8	-22.9	-23.0	-23.000	-9.970	-21.092	×	0.0%			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					210	2.7	2.97	0	0	3.08	3.02	2.98	3.33	3.212
950FF	-19.5	-20.0	-18.6	-19.7	-9.8	-20.2	-19.3	-20.0	-18.8	-20.200	-9.830	-18.394	○	-		CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					215	2.79	3.28	0	0	3.65	3.31	3.29	3.46	3.373
960	2.7	1.6	3.9	3.1	2.2	1.4	-2.8	-0.4	-4.1	-2.820	3.900	1.471	×	-19.3%		400-395	0.000	0.219	0.265	0.272	0.291	0.256	0.251	0.227	0.258	0.000	0.291	0.223	○	-					220	2.87	3.28	3.47	3.7	3.71	3.35	3.34	3.52	3.562
AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C)					410-400	0.035	0.118	0.148	0.148	0.151	0.112	0.130	0.138	0.109	0.035	0.151	0.122	○	-					230	4.39	4.98	4.99	5.28	5.29	5.16	4.89	5.11	4.643
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate		420-410	0.223	0.224	0.218	0.233	0.215	0.214	0.195	0.211	0.234	0.195	0.233	0.217	×	2.3%					240	2.69	3.1	3.28	3.5	3.51	3.16	3.15	3.33	3.379
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					430-420	1.235	0.849	0.796	0.715	0.701	0.637	0.861	1.657	1.216	0.637	1.657	0.931	○	-
CASE#	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)					600-430	4.701	4.193	5.229	5.065	5.772	4.711	4.688	4.234	4.250	4.193	5.772	4.824	○	-
600FF	25.1	25.4	24.6	25.5	25.9	25.2	24.5	24.2	25.2	24.220	25.930	25.060	○	-		440-600	-1.648	-1.541		-1.774	-1.936	-1.821	-1.800	-1.534	-1.605	-1.936	-1.534	-1.722	○	-
900FF	25.5	25.9	24.7	25.5	25.7	25.2	24.5	24.5	25.3	24.450	25.930	25.177	○	-
650FF	18.2	18.7	19.1	19.0	19.6	18.4	18.0	18.4	18.7	17.990	19.620	18.669	○	-		HIGH MASS DIAGNOSTIC TESTS
950FF	14.1	14.3	14.3	15.0	14.3	14.0	14.5	14.6	14.7	14.000	14.970	14.391	○	-		ANNUAL HEATING [MWH]
960	27.5	27.7	28.0	28.7	28.5	28.0	29.0	26.4	27.9	26.430	28.960	27.979	○	-			ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					195	0.65	0.73	0.62	0.85	0.81	0.8	0.79	0.79	0.758	Low mass peak heating (A) / kW
				CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					200	0.86	1.02	0	0	1.11	1.11	1.1	1.13	1.093
				800-430	-0.561	-0.535	-0.599	-0.567	-0.586	-0.501	-0.560	-0.649	-0.558	-0.649	-0.501	-0.570	○	-					210	0.48	1.02	0	0	1.1	1.1	1.07	1.14	0.949
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5					900-800	-3.698	-4.343	-5.356	-4.714	-4.612	-4.431	-4.285	-3.820	-4.820	-5.356	-3.698	-4.407	○	-					215	1.01	1.17	0	0	1.35	1.22	1.18	1.19	1.221
CASE 600 OR 900					900-810	-0.669	-0.836		-1.107	-0.840	-0.992	-0.912	-0.921	-0.844	-1.107	-0.669	-0.897	○	-					220	0.56	1.17	0.94	1.34	1.34	1.22	1.18	1.21	1.048
SOUTH SURFACE					910-610	-2.780	-2.944	-3.532	-3.106	-3.338	-2.908	-2.873	-3.163	-3.006	-3.532	-2.780	-3.081	○	-					230	1.06	1.65	1.46	1.88	1.88	1.7	1.71	1.75	1.411
(USE COLUMN B ONLY)					920-620	-1.300	-1.297	-1.689	-1.461	-1.676	-1.329	-1.297	-1.428	-1.391	-1.689	-1.297	-1.435	○	-					240	0.74	1.35	1.12	1.54	1.54	1.4	1.36	1.4	1.231
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average				930-630	-0.907	-1.012	-1.134	-1.128	-1.273	-0.927	-0.884	-0.712	-0.994	-1.273	-0.712	-0.997	○	-
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX					940-640	-1.958	-1.867	-2.304	-2.024	-2.392	-1.886	-1.963	-1.986	-1.901	-2.392	-1.867	-2.048	○	-
HOUR	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2					ANNUAL COOLING [MWH]
1		0	0	0	0	0	0	0	0.00	0	0	0.000					ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
2		0	0	0	0	0	0	0	0.00	0	0	0.000				CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
3		0	0	0	0	0	0	0	0.00	0	0	0.000				800-430	-0.429	-0.393	-0.367	-0.432	-0.462	-0.368	-0.410	-0.550	-0.531	-0.550	-0.367	-0.426	○	-
4		0	0	0	0	0	0	0	0.00	0	0	0.000				900-800	2.019	2.376	2.400	2.893	3.193	2.377	2.278	2.274	2.161	2.019	3.193	2.476	○	-					250	4.75	5.74	7.02	6.61	6.65	5.97	5.76	5.74	6.746
5		0	0	0	0	0	0	0	0.00	0	0	0.000				900-810	1.080	1.195		1.454	1.707	1.265	1.294	0.975	1.266	0.975	1.707	1.281	○	-					270	4.51	4.93	0	5.48	5.92	5.07	5.05	5.49	5.423	Low mass peak cooling (A) / kW
6		0	0	0	0	0	0	0	0.00	0	0	0.000				910-610	-3.094	-3.318	-3.876	-3.576	-3.924	-3.336	-3.275	-3.739	-3.509	-3.924	-3.094	-3.517	○	-					280	4.68	5.13	0	5.94	6.15	5.36	5.28	5.84	5.742
7		1.5	3.0	3.02	1.60	3	3.05	3	3.05	1.5	3.05	2.602				920-620	-1.577	-1.476	-1.894	-1.690	-1.912	-1.554	-1.483	-1.738	-1.622	-1.912	-1.476	-1.666	○	-					290	4.58	4.96	0	5.54	5.94	5.16	5.13	5.51	5.463
8		12.59	20.6	20.59	13.80	21	20.69	20.68	20.62	12.59	21	18.571				930-630	-1.090	-1.174	-1.223	-1.320	-1.463	-1.050	-1.000	-0.827	-1.144	-1.463	-0.827	-1.143	○	-					300	4.76	5.08	0	5.69	5.96	5.66	5.12	5.79	5.585
9		30.01	38.9	38.83	31.60	39	38.94	38.94	38.86	30.01	39	36.601				940-640	-3.873	-3.647	-4.419	-3.990	-4.570	-3.758	-3.863	-3.992	-3.793	-4.570	-3.647	-4.014	○	-					310	5.22	5.33	0	5.94	6.17	6.15	5.61	7.14	5.967
10		46.23	54.6	54.53	48.30	55	54.67	54.56	54.54	46.23	55	52.551				950-650	-4.429	-4.614	-5.257	-4.973	-5.956	-4.537	-4.558	-4.685	-4.465	-5.956	-4.429	-4.876	○	-					320	3.86	4.21	0	4.76	5.14	4.34	4.35	4.84	4.655
11		59.31	66.0	54.77	61.60	66	66.08	65.99	65.95	54.77	66.08	62.818				PEAK HEATING [KW]
12		65.05	71.8	59.65	69.30	72	71.92	71.74	71.77	59.65	72	68.778					ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
13		66.98	72.3	60.10	71.70	72	72.42	72.3	72.28	60.1	72.42	69.683				CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
14		63.11	66.4	55.24	68.10	66	66.53	66.38	66.41	55.24	68.1	64.538				800-430	-0.215	-0.151	-0.141	-0.149	-0.113	-0.142	-0.144	-0.198	-0.162	-0.215	-0.113	-0.157	○	-
15		51.79	54.9	45.68	58.90	55	55	54.8	54.91	45.68	58.9	53.724				900-800	-0.377	-0.340	-0.352	-0.378	-0.107	-0.294	-0.269	-0.142	-0.373	-0.378	-0.107	-0.282	○	-
16		37.13	38.9	32.37	44.40	39	38.94	38.84	38.90	32.37	44.4	38.509				900-810	-0.129	-0.113		-0.155	-0.034	-0.101	-0.089	-0.166	-0.091	-0.166	-0.034	-0.112	○	-
17		19.14	20.5	17.06	26.90	20	20.52	20.46	20.49	17.06	26.9	20.651				910-610	-0.579	-0.485	-0.470	-0.494	-0.223	-0.419	-0.386	-0.553	-0.446	-0.579	-0.223	-0.451	○	-					250	3.21	2.55	2.18	2.92	2.93	2.49	2.68	3.38	3.132
18		4.62	3.0	2.54	8.70	3	3.05	0	3.06	0	8.7	3.565				920-620	-0.283	-0.238	-0.241	-0.264	-0.150	-0.248	-0.214	-0.318	-0.247	-0.318	-0.150	-0.244	○	-					270	7.53	8.67	0	9.63	10.35	8.8	8.76	8.71	8.544
19		0	0	0	0	0	0	0	0.00	0	0	0.000				930-630	-0.237	-0.209	-0.193	-0.238	-0.141	-0.214	-0.178	-0.191	-0.221	-0.238	-0.141	-0.200	○	-					280	4.87	5.9	0	6.51	7.11	5.81	5.76	6.26	5.643	Low mass annual heating (A) / MWh
20		0	0	0	0	0	0	0	0.00	0	0	0.000				940-640	-1.252	-0.458	-0.278	-0.414	1.845	-0.230	-0.600	-0.526	-0.207	-1.252	1.845	-0.239	○	-					290	5.2	7.01	0	7.72	8.09	6.9	6.7	7.43	6.945
21		0	0	0	0	0	0	0	0.00	0	0	0.000				PEAK COOLING [KW]					300	4.3	5.84	0	6.53	7.1	5.85	5.72	5.78	5.664
22		0	0	0	0	0	0	0	0.00	0	0	0.000					ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate					310	2.73	4.57	0	5.14	5.47	3.88	3.73	2.47	3.799
23		0	0	0	0	0	0	0	0.00	0	0	0.000				CASES	UK-DMU	US/IT	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX					320	5.06	5.91	0	6.58	7.3	5.91	5.96	5.66	5.748
24		0	0	0	0	0	0	0	0.00	0	0	0.000				800-430	-0.908	-0.805	-0.684	-0.410	-0.397	-0.547	-0.816	-1.220	-0.650	-1.220	-0.397	-0.723	○	-
				900-800	2.303	2.188	2.715	2.519	3.519	2.306	2.584	2.099	2.014	2.099	3.519	2.529	×	-6.0%
				900-810	1.036	0.798	3.458	0.880	1.277	0.902	1.223	0.595	1.067	0.595	3.458	1.271	○	-
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5					910-610	-3.773	-3.324	-3.728	-3.094	-3.242	-3.384	-2.883	-2.999	-3.200	-3.773	-2.883	-3.303	○	-
CASE 600 OR 900					920-620	-1.249	-1.142	-1.321	-1.106	-1.182	-1.226	-1.225	-1.591	-1.069	-1.591	-1.106	-1.255	×	7.6%
WEST SURFACE					930-630	-1.199	-1.158	-1.200	-1.036	-1.197	-1.179	-1.110	-1.242	-0.874	-1.242	-1.036	-1.165	×	78.4%
(USE COLUMN B ONLY)					940-640	-3.273	-2.737	-3.118	-2.905	-2.636	-2.916	-2.875	-3.314	-2.827	-3.314	-2.636	-2.972	○	-					250	2.87	3.28	3.47	3.7	3.71	3.34	3.34	3.53	3.561
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average				950-650	-3.998	-3.210	-3.852	-3.501	-3.610	-3.466	-3.692	-3.812	-3.597	-3.998	-3.210	-3.643	○	-					270	2.86	3.28	0	3.67	3.71	3.34	3.34	3.74	3.476
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX					280	2.86	3.28	0	3.69	3.71	3.34	3.34	3.76	3.478
HOUR	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2					290	2.86	3.28	0	3.67	3.71	3.34	3.33	3.74	3.476
1		0	0	0	0	0	0	0	0.00	0	0	0.000				ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS					300	3.01	3.28	0	3.69	3.71	3.6	3.33	3.77	3.479	Low mass annual cooling (A) / MWh
2		0	0	0	0	0	0	0	0.00	0	0	0.000				CODENAME:		ESP			BLAST			DOE2			SRES/SUN			SERIRES			S3PAS			TRNSYS			TASE			YOUR					310	3.02	3.28	0	3.67	3.71	3.6	3.33	3.77	3.480
3		0	0	0	0	0	0	0	0.00	0	0	0.000				COUNTRY:		UK-DMU			USA/ITALY			USA			USA			UK-BRE			SPAIN			BEL/UK			FINLAND			DATA		RANGE	RANGE				320	2.86	3.28	0	3.66	3.71	3.34	3.34	3.74	3.472
4		0	0	0	0	0	0	0	0.00	0	0	0.000				CASE#	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	MIN	MAX
5		0	0	0	0	0	0	0	0.00	0	0	0.000				600	3.437	TT.January	5	3.940	JAN 04	5	4.045	JAN 04	5	4.258	JAN 04	2	4.307	01.JJJJ	2	4.037	JAN 04	2	3.931	Jan-04	6	4.354	JAN 04	2	3.831	Jan-04	02:30	3.437	4.354
6		0	0	0	0	0	0	0	0.00	0	0	0.000				610	3.437	TT.January	5	3.941	JAN 04	5	4.034	JAN 04	5	4.258	JAN 04	2	4.306	01.JJJJ	2	4.037	JAN 04	2	3.922	Jan-04	6	4.354	JAN 04	2	3.831	Jan-04	02:30	3.437	4.354
7		1.8	3.0	3	1.60	3	2.99	3	2.99	1.6	3	2.627				620	3.591	TT.January	6	3.941	JAN 04	5	4.046	JAN 04	5	4.277	JAN 04	2	4.306	01.JJJJ	2	4.277	JAN 04	2	3.922	Jan-04	6	4.379	JAN 04	2	3.837	Jan-04	02:30	3.591	4.379
8		13.92	20.2	20.24	13.50	20	20.17	20.15	20.21	13.5	20.24	18.309				630	3.592	TT.January	7	3.941	JAN 04	5	4.025	JAN 04	5	4.280	JAN 04	2	4.306	01.JJJJ	2	4.278	JAN 04	2	3.922	Jan-04	6	4.379	JAN 04	2	3.837	Jan-04	02:30	3.592	4.278
9		31.75	38.0	38.01	31	38	37.92	37.9	37.98	31	38.01	36.076				640	5.232	TT.January	7	5.486	JAN 04	8	5.943	JAN 04	8	6.530	JAN 04	8	8.078	01.JJJJ	8	6.347	JAN 04	8	5.722	Jan-04	8	6.954	JAN 04	8	5.915	Jan-04	07:30	5.232	6.954
10		45.24	53.2	53.27	47.10	53	53.17	53.15	53.27	45.24	53.27	51.168				650					250	3.36	3.04	2.61	2.59	2.58	2.26	3.23	4.91	3.014
11		56.63	64.5	53.37	59.70	64	64.39	64.4	64.48	53.37	64.47	60.994				900	2.850	TT.January	7	3.453	JAN 04	7	3.557	JAN 04	7	3.760	JAN 04	7	4.081	01.JJJJ	7	3.608	JAN 04	8	3.517	Jan-04	7	3.797	JAN 04	7	3.384	Jan-04	06:30	2.850	3.797				270	6.36	6.64	0	7.16	7.97	6.82	6.76	6.87	6.559
12		61.58	70.0	57.91	67.40	70	69.89	69.95	69.99	57.91	70	66.673				910	2.858	TT.January	7	3.456	JAN 04	7	3.564	JAN 04	7	3.764	JAN 04	7	4.083	01.JJJJ	7	3.618	JAN 04	8	3.536	Jan-04	7	3.801	JAN 04	7	3.385	Jan-04	06:30	2.858	3.801				280	4.44	4.63	0	5.22	5.76	4.63	4.79	5.24	4.679
13		63.7	70.8	58.30	70.10	71	70.75	71.16	70.67	58.3	71.16	67.974				920	3.308	TT.January	7	3.703	JAN 04	7	3.805	JAN 04	7	4.013	JAN 04	7	4.156	01.JJJJ	7	4.029	JAN 04	7	3.708	Jan-04	7	4.061	JAN 04	7	3.590	Jan-04	06:30	3.308	4.061				290	6.27	6.56	0	6.91	7.79	6.7	6.2	6.62	6.476
14		61.46	65.7	54.15	67.30	66	65.69	66.02	65.52	54.15	67.3	63.755				930	3.355	TT.January	7	3.732	JAN 04	7	3.832	JAN 04	7	4.042	JAN 04	7	4.165	01.JJJJ	7	4.064	JAN 04	7	3.744	Jan-04	7	4.188	JAN 04	8	3.617	Jan-04	06:30	3.355	4.064				300	3.4	4.09	0	4.64	5.07	4.34	4.28	4.93	4.051
15		51.67	54.9	45.38	58.90	55	55.03	55.16	54.80	45.38	58.9	53.723				940	3.980	TT.January	7	5.028	JAN 04	8	5.665	JAN 04	8	6.116	JAN 04	8	9.923	01.JJJJ	8	6.117	JAN 04	8	5.122	Jan-03	9	6.428	JAN 04	8	5.708	Jan-04	07:30	3.980	6.428				310	2.85	3.75	0	4.19	4.67	3.67	3.59	3.43	3.095	Low mass peak heating (A) / kW
16		37.2	39.5	32.70	44.90	40	39.61	39.73	39.39	32.7	44.9	39.090				950	0.000			0.000			0.000			0.000			0.000			0.000			0.000			0.000					320	5.7	5.95	0	6.48	7.33	6.18	6.18	6.14	5.936
17		16.72	21.3	17.70	27.60	21	21.42	21.6	21.24	16.72	27.6	21.047				960	2.410	TT.January	7	2.751	JAN 04	8	2.727	JAN 04	8	2.863	JAN 04	8	2.896	01.JJJJ	8	2.852	JAN 04	8	2.522	Jan-04	8	2.779	JAN 04	8	2.643	Jan-04	07:30	2.410	2.896
18		2.52	3.3	2.73	9	3	3.28	0	3.24	0	9	3.400				990	2.769	TT.February	2	3.734	JAN 04	7	3.427	JAN 04	7	3.681	JAN 04	7	3.738	Feb-06	2	3.799	JAN 04	8				4.296	JAN 04	7	3.103	Feb-06	01:30
19		0	0	0	0	0	0	0	0.00	0	0	0.000				195	2.004	TT.January	2	2.186	JAN 04	8	2.320	JAN 04	3	2.385	JAN 04	3	2.235	01.JJJJ	3	2.221	JAN 04	4	2.186	Jan-04	3	2.263	JAN 04	3	2.209	Jan-04	02:30
20		0	0	0	0	0	0	0	0.00	0	0	0.000				200	2.651	TT.January	5	2.973	JAN 04	5					3.047	01.JJJJ	3	2.999	JAN 04	2	2.969	Jan-04	5	3.382	JAN 04	2	3.035	Jan-04	02:30
21		0	0	0	0	0	0	0	0.00	0	0	0.000				210	2.701	TT.January	5	2.973	JAN 04	5					3.077	01.JJJJ	3	3.020	JAN 04	2	2.981	Jan-04	5	3.325	JAN 04	2	3.212	Jan-04	02:30
22		0	0	0	0	0	0	0	0.00	0	0	0.000				215	2.787	TT.January	5	3.280	JAN 04	5					3.650	01.JJJJ	2	3.307	JAN 04	6	3.294	Jan-04	6	3.458	JAN 04	8	3.373	Jan-04	02:30
23		0	0	0	0	0	0	0	0.00	0	0	0.000				220	2.867	TT.January	5	3.280	JAN 04	5	3.465	JAN 04	5	3.695	JAN 04	2	3.709	01.JJJJ	2	3.348	JAN 04	8	3.336	Jan-04	6	3.520	JAN 04	2	3.562	Jan-04	02:30					395	4.98	4.8	5.84	5.2	5.2	4.97	4.86	4.84	5.401
24		0	0	0	0	0	0	0	0.00	0	0	0.000				230	4.386	TT.January	5	4.984	JAN 04	2	4.994	JAN 04	2	5.279	JAN 04	2	5.293	01.JJJJ	2	5.159	JAN 04	2	4.892	Jan-04	6	5.107	JAN 04	2	4.643	Jan-04	02:30					400	6.9	7.08	8.77	7.97	7.97	7.29	7.17	7.33	8.381
				240	2.685	TT.January	5	3.100	JAN 04	5	3.282	JAN 04	5	3.495	JAN 04	2	3.509	01.JJJJ	2	3.159	JAN 04	8	3.153	Jan-04	6	3.333	JAN 04	8	3.379	Jan-04	02:30					410	8.6	8.87	10.51	9.73	9.73	9.02	8.94	9.09	9.599
				250	2.866	TT.January	5	3.279	JAN 04	5	3.465	JAN 04	5	3.695	JAN 04	2	3.709	01.JJJJ	2	3.341	JAN 04	6	3.336	Jan-04	6	3.525	JAN 04	2	3.561	Jan-04	02:30					420	7.3	7.61	9.15	8.37	8.37	7.77	7.7	7.86	8.266
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27					270	2.863	TT.January	5	3.277	JAN 04	5				3.670	JAN 04	2	3.714	01.JJJJ	2	3.340	JAN 04	6	3.336	Jan-04	6	3.738	JAN 04	2	3.476	Jan-04	02:30					430	5.43	6.49	7.83	7.18	7.19	6.66	6.5	6.51	6.923
CASE 600					280	2.864	TT.January	5	3.278	JAN 04	5				3.685	JAN 04	2	3.714	01.JJJJ	2	3.341	JAN 04	6	3.336	Jan-04	6	3.759	JAN 04	2	3.478	Jan-04	02:30					440	4.45	4.99	0	5.65	5.81	5.15	5.1	5.64	5.012
SOUTH SURFACE					290	2.863	TT.January	5	3.277	JAN 04	5				3.670	JAN 04	2	3.714	01.JJJJ	2	3.340	JAN 04	6	3.328	Jan-04	6	3.738	JAN 04	2	3.476	Jan-04	02:30					800	4.87	5.95	7.23	6.61	6.6	6.16	5.94	5.86	6.365
(USE COLUMN B ONLY)					300	3.014	TT.January	6	3.276	JAN 04	5				3.685	JAN 04	2	3.714	01.JJJJ	2	3.599	JAN 04	5	3.328	Jan-04	6	3.770	JAN 04	2	3.479	Jan-04	02:30					810	1.84	2.45	0	3	2.83	2.72	2.57	2.96	2.390	Low mass peak cooling (A) / kW
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average				310	3.015	TT.January	6	3.277	JAN 04	5				3.672	JAN 04	2	3.714	01.JJJJ	2	3.599	JAN 04	5	3.328	Jan-04	6	3.771	JAN 04	2	3.480	Jan-04	02:30
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX					320	2.861	TT.January	5	3.275	JAN 04	5				3.661	JAN 04	2	3.714	01.JJJJ	2	3.340	JAN 04	6	3.336	Jan-04	6	3.735	JAN 04	3	3.472	Jan-04	02:30
HOUR	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2					395	2.062	TT.January	7	2.209	JAN 04	8	2.328	JAN 04	3	2.385	JAN 04	3	2.391	01.JJJJ	3	2.263	JAN 04	4	2.221	Jan-04	8	2.270	JAN 04	3	2.337	Jan-04	02:30
1		0	0	0	0	0	0	0	0.00	0	0	0.000				400	2.867	TT.January	5	3.280	JAN 04	5	3.476	JAN 04	5	3.695	JAN 04	2	3.709	01.JJJJ	2	3.342	JAN 04	8	3.336	Jan-04	6	3.520	JAN 04	2	3.562	Jan-04	02:30
2		0	0	0	0	0	0	0	0.00	0	0	0.000				410	3.625	TT.January	5	4.124	JAN 04	5	4.233	JAN 04	5	4.487	JAN 04	2	4.501	01.JJJJ	2	4.227	JAN 04	2	4.114	Jan-04	6	4.314	JAN 04	2	4.103	Jan-04	02:30
3		0	0	0	0	0	0	0	0.00	0	0	0.000				420	3.443	TT.January	5	3.944	JAN 04	5	4.050	JAN 04	5	4.287	JAN 04	2	4.301	01.JJJJ	2	4.044	JAN 04	2	3.931	Jan-04	6	4.126	JAN 04	2	3.920	Jan-04	02:30					395	0	0.01	0	0.02	0.01	0.01	0.01	0.01	0.000
4		0	0	0	0	0	0	0	0.00	0	0	0.000				430	3.442	TT.January	5	3.944	JAN 04	5	4.050	JAN 04	5	4.287	JAN 04	2	4.301	01.JJJJ	2	4.044	JAN 04	2	3.931	Jan-04	6	4.137	JAN 04	2	3.920	Jan-04	02:30					400	0	0.04	0	0.06	0.06	0.04	0.04	0.04	0.004
5		0	0.2	0.14	0.50	0	0.17	0.2	0.17	0	0.5	0.168				440	3.439	TT.January	5	3.942	JAN 04	5				4.277	JAN 04	2	4.306	01.JJJJ	2	4.041	JAN 04	2	3.931	Jan-04	6	4.376	JAN 04	2	3.836	Jan-04	02:30					410	0	0.06	0.01	0.08	0.08	0.06	0.07	0.07	0.011
6		20.11	27.8	29.94	17.90	28	27.01	25.7	26.16	17.9	29.94	25.213				800	3.227	TT.January	5	3.793	JAN 04	7	3.909	JAN 04	7	4.138	JAN 04	2	4.188	01.JJJJ	8	3.902	JAN 04	8	3.786	Jan-04	7	3.939	JAN 04	7			00:00					420	0.01	0.15	0.05	0.19	0.19	0.15	0.16	0.14	0.055
7		70.22	77.3	89.20	58.60	80	63	62.1	81.04	58.6	89.2	71.489				810	2.979	TT.January	7	3.566	JAN 04	7				3.915	JAN 04	7	4.115	01.JJJJ	7	3.709	JAN 04	8	3.606	Jan-04	7	3.963	JAN 04	7			00:00					430	0.54	0.62	0.42	0.7	0.68	0.56	0.62	0.88	0.801
8		108.13	100.0	112.85	100.40	104	71.22	107.47	106.96	71.22	112.85	100.580				ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS					440	3.97	4.17	0	4.67	5.2	3.99	3.98	4.68	4.109
9		219.58	211.0	164.86	205.90	217	187.72	232.33	210.67	164.86	232.33	205.485				CODENAME:		ESP			BLAST			DOE2			SRES/SUN			SERIRES			S3PAS			TRNSYS			TASE			YOUR					800	0.11	0.22	0.06	0.27	0.22	0.2	0.21	0.33	0.270
10		343.67	331.0	291.84	326	336	314.17	349.16	331.55	291.84	349.16	327.407				COUNTRY:		UK-DMU			USA/ITALY			USA			USA			UK-BRE			SPAIN			BEL/UK			FINLAND			DATA		RANGE	RANGE				810	1.05	1.41	0	1.71	1.71	1.31	1.19	1.62	1.165
11		435.54	418.2	389.26	415.10	423	404.44	430.22	419.90	389.26	435.54	416.533				CASE#	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE	HR	KW	DATE		KW	DATE	HR	KW	DATE	HR	MIN	MAX					Realistic case annual heating (B) / MWh
12		475.37	455.0	437.20	454.80	459	443.61	459.85	458.03	437.2	475.37	454.975				600	6.194	TT.October	13	5.965	OCT 16	14	6.656	OCT 16	13	6.827	OCT 16	14	7.551	10.JJJJ	13	6.286	NOV 25	-6.19	6.486	Oct-16	14	6.812	OCT 17	14	6.184	Oct-16	13:30	5.965	6.812
13		488.49	464.6	455.75	455.60	469	452.50	462.28	469.06	452.5	488.49	464.027				610	5.669	TT.November	13	5.824	NOV 25	14	6.064	JAN 13	14	6.371	NOV 25	14	7.215	11.JJJJ	13	6.170	NOV 25	-5.67	5.675	11.JJJJ	14	6.146	OCT 17	14	5.957	Nov-25	13:30	5.669	6.146
14		443.66	413.6	413.67	408.60	418	400.56	404.57	419.41	400.56	443.66	414.671				620	3.634	TT.July	16	4.075	JUL 26	17	4.430	JUL 26	17	4.593	JUL 26	17	4.959	07.JJJJ	10	4.297	JUL 26	-3.63	4.275	07.JJJJ	17	5.096	JUL 26	16	4.075	Jul-26	16:30	3.634	5.096
15		367.07	334.3	341.53	321.20	340	316.94	319.26	341.29	316.94	367.07	334.326				630	3.072	TT.July	16	3.704	JUL 26	17	3.588	JUL 26	17	4.116	JUL 26	17	4.400	07.JJJJ	9	3.665	JUL 26	-3.07	3.608	07.JJJJ	17	3.546	JUN 30	16	3.121	Jul-26	16:30	3.072	3.704
16		246.71	211.9	223.71	200.60	218	188.89	193.61	219.37	188.89	246.71	211.923				640	6.161	TT.October	13	5.892	OCT 16	14	6.576	OCT 16	14	6.776	OCT 16	14	7.537	10.JJJJ	13	6.250	NOV 25	-6.16	6.442	Oct-16	14	6.771	OCT 17	16	6.125	Oct-16	13:30					395	2.06	2.21	2.33	2.39	2.39	2.26	2.22	2.27	2.337
17		119.19	111.7	105.72	102.30	115	86.03	132.3	108.82	86.03	132.3	110.326				650	6.031	TT.October	13	5.831	OCT 16	14	6.516	OCT 16	14	6.671	OCT 16	14	7.458	10.JJJJ	13	6.143	NOV 25	-6.03	6.378	Oct-17	14	6.679	OCT 17	16	6.019	Oct-16	13:30	5.831	6.679				400	2.87	3.28	3.48	3.7	3.71	3.34	3.34	3.52	3.562
18		68.86	73.1	68.47	78.80	74	69.78	76.6	72.58	68.47	78.8	72.798				900	2.888	TT.October	14	3.155	OCT 06	15	3.458	OCT 17	14	3.871	OCT 17	14	4.901	10.JJJJ	14	3.334	OCT 17	-2.89	3.567	Oct-17	15	3.457	OCT 17	16	3.298	Oct-17	14:30	2.888	3.567				410	3.63	4.12	4.23	4.49	4.5	4.23	4.11	4.31	4.103
19		19.75	17.7	14.35	37.10	18	17.61	18.05	17.65	14.35	37.1	20.366				910	1.896	TT.October	15	2.500	OCT 21	15	2.336	OCT 17	15	3.277	OCT 17	15	3.973	10.JJJJ	15	2.786	OCT 17	-1.9	2.792	Oct-17	15	3.147	OCT 17	16	2.757	Oct-17	14:30	1.896	3.147				420	3.44	3.94	4.05	4.29	4.3	4.04	3.93	4.13	3.920
20		0	0	0	1.10	0	0	0	0.00	0	1.1	0.157				920	2.385	TT.July	16	2.933	JUL 26	17	3.109	JUL 26	17	3.487	JUL 26	17	3.777	07.JJJJ	17	3.071	JUL 26	-2.39	3.050	07.JJJJ	17	3.505	JUL 26	16	3.006	Jun-30	16:30	2.385	3.505				430	3.44	3.94	4.05	4.29	4.3	4.04	3.93	4.14	3.920
21		0	0	0	0	0	0	0	0.00	0	0	0.000				930	1.873	TT.July	17	2.546	JUL 26	17	2.388	JUL 26	18	3.080	JUL 26	17	3.203	07.JJJJ	17	2.486	JUL 26	-1.87	2.498	07.JJJJ	17	2.304	JUN 30	16	2.246	Jul-26	16:30	1.873	2.546				440	3.44	3.94	0	4.28	4.31	4.04	3.93	4.38	3.836
22		0	0	0	0	0	0	0	0.00	0	0	0.000				940	2.888	TT.October	14	3.155	OCT 06	15	3.458	OCT 17	14	3.871	OCT 17	14	4.901	10.JJJJ	14	3.334	OCT 17	-2.89	3.567	Oct-17	15	3.457	OCT 17	16	3.298	Oct-17	14:30					800	3.23	3.79	3.91	4.14	4.19	3.9	3.79	3.94	3.758
23		0	0	0	0	0	0	0	0.00	0	0	0.000				950	2.033	TT.September	14	2.621	SEP 02	15	2.664	SEP 2	15	3.170	SEP 02	14	3.848	09.JJJJ	15	2.677	SEP 02	-2.03	2.686	Sep-02	15	2.867	SEP 02	16	2.422	Sep-02	13:30	2.033	2.867				810	2.98	3.57	0	3.92	4.12	3.71	3.61	3.96	3.476
24		0	0	0	0	0	0	0	0.00	0	0	0.000				960	0.953	TT.August	16	1.144	JUL 26	16	1.057	JUL 26	16	1.370	JUL 26	16	1.306	07.JJJJ	16	1.179	JUL 26	16	1.378	07.JJJJ	16	1.403	JUL 26	16	1.064	Jul-27	15:30	0.953	1.403
				990	2.422	TT.October	14	2.912	SEP 02	14	3.436	OCT 17	13	2.819	SEP 02	14	3.525	10.JJJJ	14	1.859	NOV 25	14				2.779	SEP 02	16	2.124	Oct-17	13:30					Realistic case annual cooling (B) / MWh
				195	0.651	TT.July	15	0.728	JUL 26	16	0.616	JUL 27	15	0.853	JUL 26	16	0.806	07.JJJJ	16	0.799	JUL 26	-0.65	0.791	07.JJJJ	16	0.790	JUL 26	16	0.758	Jul-26	15:30
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27					200	0.863	TT.August	14	1.017	JUL 26	15					1.111	07.JJJJ	15	1.105	JUL 26	-0.86	1.101	07.JJJJ	16	1.126	JUL 26	16	1.093	Jul-27	14:30
CASE 600					210	0.476	TT.August	16	1.017	JUL 26	15					1.101	07.JJJJ	15	1.097	JUL 26	-0.48	1.068	07.JJJJ	16	1.142	JUL 26	16	0.949	Jul-27	14:30
WEST SURFACE					215	1.007	TT.August	14	1.166	JUL 26	15					1.347	07.JJJJ	15	1.216	JUL 26	-1.01	1.184	07.JJJJ	16	1.192	JUL 26	16	1.221	Jul-26	15:30					395	0	0.36	0	0.39	0.42	0.36	0.36	0.35	0.117
(USE COLUMN B ONLY)					220	0.560	TT.July	15	1.166	JUL 26	15	0.937	JUL 27	14	1.340	JUL 26	15	1.342	07.JJJJ	15	1.215	JUL 26	-0.56	1.179	07.JJJJ	16	1.213	JUL 26	16	1.048	Jul-27	14:30					400	0	0.58	0.27	0.67	0.71	0.61	0.61	0.57	0.375
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average				230	1.059	TT.July	15	1.646	JUL 26	15	1.455	JUL 27	14	1.875	JUL 26	15	1.878	07.JJJJ	15	1.700	JUL 26	-1.06	1.708	07.JJJJ	16	1.749	JUL 26	16	1.411	Jul-27	14:30					410	0.04	0.7	0.41	0.81	0.86	0.72	0.74	0.71	0.484
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX					240	0.739	TT.July	15	1.347	JUL 26	15	1.119	JUL 27	14	1.540	JUL 26	15	1.542	07.JJJJ	15	1.398	JUL 26	-0.74	1.361	07.JJJJ	16	1.397	JUL 26	16	1.231	Jul-27	14:30					420	0.26	0.92	0.63	1.05	1.08	0.94	0.94	0.92	0.718
HOUR	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2	Wh/m2					250	3.360	TT.September	12	3.036	SEP 05	12	2.605	SEP 5	11	2.590	AUG 26	14	2.582	08.JJJJ	12	2.258	AUG 26	-3.36	3.228	Sep-05	13	4.912	SEP 05	16	3.014	Jun-30	12:30					430	1.49	1.77	1.43	1.76	1.78	1.58	1.8	2.58	1.933
1		0	0	0	0	0	0	0	0.00	0	0	0.000				270	6.356	TT.November	13	6.641	NOV 25	14				7.163	OCT 16	14	7.967	11.JJJJ	13	6.819	NOV 25	-6.36	6.764	Oct-17	14	6.867	OCT 16	16	6.559	Nov-25	12:30					440	4.55	4.42	0	5.05	5.62	4.47	4.69	5.28	4.579
2		0	0	0	0	0	0	0	0.00	0	0	0.000				280	4.444	TT.October	13	4.631	NOV 25	13				5.220	OCT 16	14	5.759	10.JJJJ	13	4.630	NOV 25	-4.44	4.786	Oct-16	14	5.236	OCT 16	16	4.679	Oct-16	13:30					800	0.59	0.97	0.74	1.35	1.38	1.03	0.98	1.36	1.284
3		0	0	0	0	0	0	0	0.00	0	0	0.000				290	6.269	TT.January	13	6.555	NOV 25	14				6.910	NOV 25	14	7.793	12.JJJJ	13	6.700	NOV 25	-6.27	6.203	11.JJJJ	14	6.621	NOV 25	16	6.476	Nov-25	13:30					810	1.85	2.36	0	2.99	3.62	2.43	2.34	2.86	2.231
4		0	0	0	0	0	0	0	0.00	0	0	0.000				300	3.404	TT.July	16	4.093	JUL 26	17				4.642	JUL 26	17	5.072	07.JJJJ	10	4.336	JUL 26	-3.4	4.278	07.JJJJ	17	4.929	JUL 26	16	4.051	Jun-30	16:30
5		0	0.2	0.14	0.40	0	0.17	0.2	0.17	0	0.4	0.154				310	2.848	TT.July	16	3.749	JUN 30	17				4.186	JUL 26	17	4.666	07.JJJJ	9	3.669	JUL 26	-2.85	3.589	07.JJJJ	17	3.425	JUN 30	16	3.095	Jul-26	16:30
6		19.96	27.8	29.94	17.90	28	27.01	25.7	26.16	17.9	29.94	25.191				320	5.701	TT.November	13	5.946	NOV 25	14				6.484	OCT 16	14	7.332	11.JJJJ	13	6.183	NOV 25	-5.7	6.178	Oct-17	14	6.141	OCT 16	16	5.936	Nov-25	13:30
7		65.86	77.3	89.20	58.50	80	63	62.1	81.04	58.5	89.2	70.852				395	0.000			0.362	JUL 26	18	0.000			0.394	JUL 26	17	0.421	07.JJJJ	16	0.356	JUL 26	18	0.363	07.JJJJ	18	0.345	JUL 26	16	0.117	Jul-27	16:30					Realistic case peak heating (B) / kW
8		97.11	100.0	112.85	91.80	104	71.22	72	106.96	71.22	112.85	92.710				400	0.000			0.581	JUL 26	17	0.265	JUL 27	17	0.666	JUL 26	16	0.712	07.JJJJ	15	0.612	JUL 26	17	0.613	07.JJJJ	17	0.572	JUL 26	16	0.375	Jul-27	16:30
9		116.89	120.1	121.41	113.70	125	85.58	92.6	127.13	85.58	125	110.747				410	0.035	TT.July	16	0.699	JUL 26	17	0.413	JUL 27	17	0.814	JUL 26	15	0.863	07.JJJJ	15	0.724	JUL 26	-0.04	0.743	07.JJJJ	17	0.710	JUL 26	16	0.484	Jul-27	15:30
10		128.97	135.0	123.51	131.20	140	98.03	112.8	141.15	98.03	140	124.210				420	0.258	TT.July	15	0.923	JUL 26	15	0.631	JUL 27	15	1.047	JUL 26	15	1.078	07.JJJJ	15	0.938	JUL 26	-0.26	0.938	07.JJJJ	16	0.921	JUL 26	16	0.718	Jul-27	15:30
11		138.05	149.6	125.06	145.70	154	109.14	136.75	153.98	109.14	154	136.898				430	1.493	TT.August	14	1.772	AUG 26	14	1.427	AUG 16	14	1.762	JUL 26	15	1.779	08.JJJJ	13	1.575	JUL 26	-1.49	1.798	09.JJJJ	13	2.578	SEP 05	16	1.933	Jul-27	13:30
12		141.34	153.1	121.07	153.80	157	113.06	150.9	155.43	113.06	157	141.472				440	4.546	TT.October	13	4.424	OCT 16	14				5.053	OCT 16	14	5.615	10.JJJJ	13	4.465	OCT 16	-4.55	4.686	Oct-16	14	5.278	OCT 17	16	4.579	Oct-16	13:30
13		243.51	266.4	117.94	267.70	270	235.17	382.5	245.86	117.94	382.5	254.753				800	0.585	TT.July	14	0.967	AUG 16	14	0.743	JUL 28	14	1.352	JUL 27	14	1.382	07.JJJJ	14	1.028	JUL 27	-0.59	0.983	Aug-16	14	1.358	SEP 05	16	1.284	Jul-27	14:30
14		462.83	461.3	333.68	464.80	463	453.89	576.81	440.65	333.68	576.81	459.470				810	1.852	TT.September	14	2.357	AUG 26	14				2.991	SEP 02	14	3.624	09.JJJJ	14	2.432	SEP 02	-1.85	2.344	Sep-02	14	2.862	SEP 02	16	2.231	Sep-02	13:30
15		664.62	635.5	525.35	635.10	635	652.50	744.52	616.06	525.35	744.52	641.800				FREE-FLOAT TEMPERATURE OUTPUT
16		786.35	719.3	634.59	738.30	715	762.78	807.29	703.76	634.59	807.29	737.662				MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
17		649.05	502.8	478.44	623.90	497	568.33	541.68	496.09	478.44	649.05	551.598				CODENAME:		ESP			BLAST			DOE2			SRES/SUN			SERIRES			S3PAS			TRNSYS			TASE			YOUR
18		243.11	141.2	140.30	296.90	139	158	145.25	140.57	139	296.9	180.543				COUNTRY:		UK-DMU			USA/ITALY			USA			USA			UK-BRE			SPAIN			BEL/UK			FINLAND			DATA
19		43.19	25.2	21.96	68.80	24	26.60	24.9	25.22	21.96	68.8	33.528				CASE#	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE		TMP (C)	DATE	HR	TMP (C)	DATE	HR
20		0	0	0	1.60	0	0	0	0.00	0	1.6	0.229				600FF	64.9	TT.October	15	65.1	OCT 16	15	69.5	OCT 17	15	68.6	OCT 16	15	69.8	10.JJJJ	16	64.9	OCT 16	16	65.3	Oct-17	16	65.3	OCT 15	16	65.5	Oct-17	14:30
21		0	0	0	0	0	0	0	0.00	0	0	0.000				900FF	41.8	TT.October	15	43.4	SEP 02	16	42.7	SEP 02	15	44.8	SEP 02	15	43.4	09.JJJJ	16	43.0	SEP 02	15	42.5	Oct-17	15	43.2	SEP 15	15	63.6	Oct-17	14:30					Realistic case peak cooling (B) / kW
22		0	0	0	0	0	0	0	0.00	0	0	0.000				650FF	63.2	TT.October	15	63.5	OCT 16	15	68.2	OCT 17	15	67.0	OCT 16	15	68.5	10.JJJJ	16	63.3	OCT 16	16	63.7	Oct-17	16	63.8	OCT 16	16	42.2	Oct-17	14:30
23		0	0	0	0	0	0	0	0.00	0	0	0.000				950FF	35.5	TT.September	16	36.2	SEP 02	16	35.9	SEP 02	16	38.5	SEP 02	15	35.7	09.JJJJ	16	36.1	SEP 02	16	35.7	Sep-02	15	37.6	SEP 15	16	35.6	Sep-02	15:30
24		0	0	0	0	0	0	0	0.00	0	0	0.000				960	48.9	TT.October	15	48.9	OCT 06	15	49.0	OCT 17	15	51.0	OCT 17	15	51.2	10.JJJJ	16	50.2	OCT 17	15	55.3	Oct-17	15	48.9	OCT 15	15	67.6	Oct-17	14:30
				MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
				CODENAME:		ESP			BLAST			DOE2			SRES/SUN			SERIRES			S3PAS			TRNSYS			TASE			YOUR
HOURLY FREE FLOAT TEMPERATURE DATA					COUNTRY:		UK-DMU			USA/ITALY			USA			USA			UK-BRE			SPAIN			BEL/UK			FINLAND			DATA
CASE 600FF JAN 4					CASE#	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE	HR	TMP (C)	DATE		TMP (C)	DATE	HR	TMP (C)	DATE	HR
(USE COLUMN B ONLY)					600FF	-15.6	TT.January	7	-17.1	JAN 04	8	-18.8	JAN 04	8	-18.0	JAN 04	7	-10.0	01.JJJJ	24	-17.8	JAN 04	8	-17.8	Jan-04	7	-18.5	JAN 08	9	-18.4	Jan-04	06:30
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average				900FF	-1.6	TT.January	8	-3.2	JAN 04	8	-4.3	JAN 04	8	-4.5	JAN 04	8	-3.9	01.JJJJ	8	-4.0	JAN 04	8	-6.4	Jan-04	8	-5.6	JAN 08	9	-23.0	Jan-04	06:30
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX					650FF	-22.6	TT.January	6	-23.0	JAN 04	7	-21.6	JAN 04	2	-23.0	JAN 04	2	-10.0	01.JJJJ	6	-22.9	JAN 04	2	-22.8	Jan-04	7	-22.9	JAN 02	23	-3.9	Jan-04	07:30
HOUR	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)					950FF	-19.5	TT.January	6	-20.0	JAN 04	7	-18.6	JAN 04	7	-19.7	JAN 04	7	-9.8	12.JJJJ	1	-20.2	JAN 04	7	-19.3	Jan-04	7	-20.0	JAN 07	22	-18.8	Jan-04	06:30
1	-12.0	-12.3	-12.21	-11.97	-8.88	-12.1	-12.02	-13.04	-11.86	-13.04	-8.88	-11.820				960	2.7	TT.February	6	1.6	FEB 06	7	3.9	FEB 06	7	3.1	FEB 06	7	2.2	02.JJJJ	7	1.4	FEB 06	6	-2.8	Jan-04	8	-0.4	FEB 05	7	-4.1	Jan-04	06:30
2	-13.5	-14.1	-13.8	-13.59	-10.48	-13.7	-13.50	-14.59	-13.54	-14.59	-10.48	-13.410				AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C)
3	-14.4	-15.4	-14.9	-14.85	-11.76	-14.7	-14.70	-15.65	-14.91	-15.65	-11.76	-14.545				CODENAME:		ESP			BLAST			DOE2			SRES/SUN			SERIRES			S3PAS			TRNSYS			TASE			YOUR
4	-15.3	-16.3	-15.79	-15.83	-12.75	-15.6	-15.65	-16.46	-15.96	-16.46	-12.75	-15.455				COUNTRY:		UK-DMU			USA/ITALY			USA			USA			UK-BRE			SPAIN			BEL/UK			FINLAND			DATA					Temperature [C] / Frequency [hour]
5	-16.0	-17.1	-16.55	-16.65	-13.69	-16.4	-16.47	-17.16	-16.89	-17.16	-13.69	-16.252				CASE#	TMP (C)			TMP (C)			TMP (C)			TMP (C)			TMP (C)			TMP (C)			TMP (C)			TMP (C)			TMP (C)
6	-16.4	-17.9	-17.2	-17.33	-14.49	-17	-17.14	-17.79	-17.70	-17.9	-14.49	-16.906				600FF	25.1			25.4			24.6			25.5			25.9			25.2			24.5			24.2			25.2
7	-17.0	-18.5	-17.74	-17.90	-15.15	-17.6	-17.70	-18.32	-18.39	-18.5	-15.15	-17.490				900FF	25.5			25.9			24.7			25.5			25.7			25.2			24.5			24.5			18.7
8	-17.1	-18.8	-17.85	-18.09	-15.63	-17.8	-17.59	-18.47	-18.38	-18.8	-15.63	-17.660				650FF	18.2			18.7			19.1			19.0			19.6			18.4			18.0			18.4			25.3
9	-13.7	-14.7	-14.88	-15.46	-14.63	-14.6	-13.46	-15.47	-14.80	-15.47	-13.46	-14.617				950FF	14.1			14.3			14.3			15.0			14.3			14.0			14.5			14.6			14.7
10	-8.0	-7.8	-9.07	-9.56	-10.03	-8.9	-7.10	-9.56	-8.89	-10.03	-7.1	-8.752				960	27.5			27.7			28.0			28.7			28.5			28.0			29.0			26.4			27.9
11	2.6	3.2	1.01	0.68	-2.20	1	3.66	0.49	1.69	-2.2	3.66	1.305
12	12.2	13.4	11.21	12.04	8.84	10.7	13.49	10.39	11.60	8.84	13.49	11.536
13	20.9	22.3	20.03	21.88	18.96	19.2	21.77	18.75	20.06	18.75	22.3	20.469
14	27.5	29.5	27.27	29.82	27.19	26.1	28.26	25.48	26.79	25.48	29.82	27.644
15	31.3	33.8	31.34	34.69	33.22	29.8	32.09	29.21	30.73	29.21	34.69	31.935
16	31.1	33.5	31.47	35.46	35.51	29.7	32.16	28.97	30.77	28.97	35.51	32.229
17	24.3	27	25.96	30.33	31.46	23.9	25.71	22.58	24.82	22.58	31.46	26.403
18	17.5	19.7	18.96	22.66	23.99	17.6	18.84	15.59	18.47	15.59	23.99	19.350
19	12.1	13.7	13.04	15.86	18.08	12.2	13.10	10.2	12.99	10.2	18.08	13.529
20	7.6	8.7	8.31	10.34	13.02	7.8	8.41	6.02	8.47	6.02	13.02	8.771
21	3.6	4.4	4.27	5.73	8.87	4	4.39	2.39	4.70	2.39	8.87	4.706
22	0.5	1	0.99	1.92	5.12	0.9	0.97	-0.59	1.44	-0.59	5.12	1.353
23	-1.9	-1.9	-1.66	-1.15	2.03	-1.7	-1.78	-3.04	-1.28	-3.04	2.03	-1.392
24	-4.1	-4.4	-3.92	-3.69	-1.03	-3.9	-4.03	-5.14	-3.67	-5.14	-1.03	-3.773

HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX
HOUR	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)
1	-0.2	-0.9	-1.31	-0.65	1.61	-0.7	-3.46	-2.68	-0.68	-3.46	1.61	-1.032
2	-0.8	-1.6	-1.97	-1.26	0.93	-1.4	-3.99	-3.33	-1.33	-3.99	0.93	-1.676
3	-1.1	-2	-2.37	-1.74	0.49	-1.8	-4.40	-3.72	-1.86	-4.4	0.49	-2.078
4	-1.7	-2.5	-2.81	-2.21	0.07	-2.3	-4.80	-4.1	-2.32	-4.8	0.07	-2.541
5	-2.0	-2.9	-3.25	-2.69	-0.41	-2.7	-5.22	-4.51	-2.79	-5.22	-0.41	-2.965
6	-2.4	-3.4	-3.68	-3.15	-0.87	-3.2	-5.60	-4.93	-3.25	-5.6	-0.87	-3.408
7	-3.0	-3.9	-4.1	-3.60	-1.27	-3.6	-5.98	-5.34	-3.70	-5.98	-1.27	-3.846
8	-3.2	-4.3	-4.4	-3.94	-1.64	-4	-6.08	-5.64	-3.94	-6.08	-1.64	-4.144
9	-2.4	-3.3	-3.45	-3.30	-1.54	-3.2	-4.72	-4.59	-3.04	-4.72	-1.54	-3.311
10	-1.1	-1.6	-1.6	-1.84	-0.40	-1.7	-2.98	-2.64	-1.53	-2.98	-0.4	-1.731
11	1.6	1.2	1.66	0.84	1.59	0.9	0.25	0.75	1.43	0.25	1.66	1.098
12	3.6	3.5	4.4	3.39	4.40	3.1	2.54	3.26	3.86	2.54	4.4	3.527
13	5.6	5.5	6.56	5.48	6.72	5.1	4.38	4.99	5.81	4.38	6.72	5.544
14	7.3	7.2	8.39	7.27	8.66	6.8	5.85	6.51	7.38	5.85	8.66	7.251
15	8.3	8	9.04	8.26	10.02	7.6	6.61	7.11	8.24	6.61	10.02	8.114
16	8.2	7.9	8.58	8.33	10.40	7.4	6.33	6.68	8.07	6.33	10.4	7.972
17	6.5	6.2	6.44	6.90	9.41	5.8	4.20	4.24	6.26	4.2	9.41	6.216
18	5.3	4.7	4.43	5.40	7.66	4.4	2.87	2.45	4.84	2.45	7.66	4.645
19	4.5	3.8	3.37	4.50	6.74	3.6	2.11	1.71	3.88	1.71	6.74	3.793
20	3.9	3.2	2.73	3.86	6	3	1.58	1.32	3.21	1.32	6	3.197
21	3.2	2.7	2.11	3.23	5.41	2.4	1.05	0.82	2.65	0.82	5.41	2.617
22	2.8	2.2	1.66	2.69	4.74	1.9	0.55	0.42	2.11	0.42	4.74	2.126
23	2.5	1.7	1.26	2.19	4.20	1.5	0.15	0.05	1.63	0.05	4.2	1.691
24	1.9	1.2	0.83	1.69	3.66	1	-0.24	-0.34	1.13	-0.34	3.66	1.213

HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FFV JULY 27
(USE COLUMN B ONLY)
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX
HOUR	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)
1	22.2	21.8	22.37	22.25	22.58	22.4	22.69	22.26	23.03	21.8	22.69	22.322
2	21.2	20.8	21.19	20.97	21.15	21.2	21.33	21.11	21.49	20.8	21.33	21.113
3	20.3	19.9	20.33	20.09	20.23	20.4	20.41	20.28	20.48	19.9	20.41	20.243
4	19.5	19.1	19.54	19.35	19.45	19.5	19.61	19.49	19.63	19.1	19.61	19.445
5	19.3	18.8	19.21	18.99	18.95	19.2	19.16	19.14	19.06	18.8	19.21	19.093
6	19.9	19.5	19.86	19.57	19.24	19.9	19.60	19.81	19.35	19.24	19.9	19.674
7	22.5	22.2	22.51	22.09	21.16	22.5	21.68	22.49	21.31	21.16	22.51	22.145
8	25.0	24	24.89	24.56	23.56	24.7	23.47	24.81	24.01	23.47	24.89	24.377
9	28.3	27.3	28.29	27.70	25.67	27.9	26.38	28.04	27.16	25.67	28.29	27.452
10	31.8	31.5	32.42	31.41	28.91	31.7	30.35	32.11	31.17	28.91	32.42	31.279
11	35.8	36.2	37.12	35.85	32.80	36.2	34.82	36.54	35.62	32.8	37.12	35.669
12	40.2	41.1	42.08	40.82	37.49	40.8	39.38	41.15	40.08	37.49	42.08	40.377
13	43.9	45.4	46.46	45.56	41.94	45	43.48	45.03	44.14	41.94	46.46	44.597
14	46.3	48.4	49.69	49.28	45.43	48.1	46.14	47.65	47.08	45.43	49.69	47.630
15	47.6	50.1	51.3	51.45	47.41	49.6	47.40	49.04	48.68	47.4	51.45	49.242
16	47.6	50.1	51.28	51.73	47.84	49.7	47.33	49.28	48.78	47.33	51.73	49.358
17	47.3	49.1	50.46	50.74	47.01	49.1	46.71	48.73	48.23	46.71	50.74	48.649
18	45.4	46.8	48.37	48.81	45.53	47.2	45.28	46.58	46.68	45.28	48.81	46.746
19	33.7	34	35.39	37.60	37.37	35.1	33.10	34.91	35.24	33.1	37.6	35.147
20	30.9	30.9	31.63	32.09	31.57	31.6	30.49	30.69	31.94	30.49	32.09	31.230
21	28.7	28.5	29.12	29.03	29.05	29.2	28.55	28.81	29.65	28.5	29.2	28.869
22	26.5	26.3	26.83	26.62	26.92	26.9	26.66	26.66	27.56	26.3	26.92	26.673
23	25.7	25.4	25.87	25.44	25.52	25.9	25.55	25.69	26.05	25.4	25.9	25.632
24	24.1	23.7	24.19	23.96	23.84	24.2	24.26	24.1	24.76	23.7	24.26	24.038

HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FFV JULY 27
(USE COLUMN B ONLY)
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX
HOUR	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)	TEMP (C)
1	24.6	24.2	24.52	25.51	24.36	24.6	25.28	24.53	24.94	24.2	25.51	24.695
2	23.9	23.5	23.81	24.74	23.46	23.9	24.47	23.8	24.00	23.46	24.74	23.947
3	23.3	22.9	23.22	24.07	22.86	23.3	23.87	23.23	23.38	22.86	24.07	23.345
4	22.7	22.3	22.6	23.39	22.27	22.7	23.26	22.6	22.79	22.27	23.39	22.725
5	22.5	22	22.32	22.96	21.86	22.4	22.87	22.27	22.35	21.86	22.96	22.392
6	22.8	22.5	22.77	23.08	22.01	22.8	23.06	22.67	22.45	22.01	23.08	22.713
7	24.7	24.3	24.73	24.37	23.32	24.6	24.38	24.55	23.66	23.32	24.73	24.365
8	27.4	26.5	27.59	25.85	25.62	27.1	27.21	27.57	26.55	25.62	27.59	26.850
9	28.3	27.5	29.09	26.81	27.59	28.2	27.98	29.42	27.66	26.81	29.42	28.114
10	29.2	28.6	30.5	27.79	28.82	29.3	29.11	30.68	28.84	27.79	30.68	29.251
11	30.2	29.8	31.98	28.96	29.84	30.5	30.31	31.91	30.06	28.96	31.98	30.436
12	31.3	31.1	33.56	30.31	30.98	31.7	31.53	33.27	31.27	30.31	33.56	31.723
13	32.2	32.2	34.79	31.54	32.08	32.8	32.55	34.27	32.38	31.54	34.79	32.802
14	32.8	33	35.65	32.52	32.85	33.6	33.15	34.9	33.13	32.52	35.65	33.564
15	33.1	33.4	35.96	33.08	33.33	34	33.37	35.19	33.55	33.08	35.96	33.931
16	33.2	33.5	35.82	33.22	33.55	34.1	33.38	35.28	33.61	33.22	35.82	34.012
17	33.4	33.5	35.61	33.18	33.44	34.1	33.37	35.3	33.62	33.18	35.61	33.982
18	33.0	33.1	34.93	32.94	33.23	33.7	33.16	34.71	33.36	32.94	34.93	33.596
19	30.2	30	30.96	30.93	30.92	30.6	30.43	30.74	30.80	30	30.96	30.598
20	29.4	29.1	29.79	29.97	29.17	29.6	29.61	29.38	29.75	29.1	29.97	29.497
21	28.5	28.2	28.83	29.17	28.31	28.7	28.89	27.64	28.93	27.64	29.17	28.535
22	27.4	27.1	27.59	28.15	27.27	27.5	27.93	27.46	27.93	27.1	28.15	27.547
23	27.2	26.8	27.28	27.72	26.62	27.3	27.42	27.1	27.21	26.62	27.72	27.177
24	26.0	25.7	26.1	26.74	25.54	26.1	26.59	26.02	26.50	25.54	26.74	26.096

HOURLY HEATING & COOLING LOAD DATA
CASE 600 JAN 4
[USE (-) FOR COOLING]
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX
HOUR	kWh	kWh	kWh	kWh	kWh	kWh	kWh	kWh
1	3.802	3.926	4.13	4.19	3.25	3.93	3.767	4.225	3.66	3.25	4.23	3.902
2	3.911	4.035	4.26	4.31	3.41	4.04	3.867	4.354	3.79	3.41	4.35	4.022
3	3.866	4.013	4.23	4.25	3.39	4	3.903	4.321	3.83	3.39	4.32	3.998
4	3.920	4.041	4.22	4.23	3.38	4	3.894	4.308	3.81	3.38	4.31	3.999
5	3.940	4.045	4.22	4.23	3.42	4	3.917	4.303	3.81	3.42	4.3	4.009
6	3.926	4.036	4.22	4.23	3.43	4	3.931	4.307	3.82	3.43	4.31	4.010
7	3.937	4.045	4.22	4.23	3.42	4	3.931	4.307	3.82	3.42	4.31	4.011
8	3.702	3.857	4.09	4.04	3.34	3.9	3.753	4.167	3.63	3.34	4.17	3.856
9	2.675	2.559	2.9	2.36	2.77	2.71	2.423	2.912	2.41	2.36	2.91	2.663
10	1.383	0.843	1.28	0.33	1.50	1.15	0.797	1.466	0.94	0.33	1.5	1.092
11	0.000	0.000	0	-0.15	0.15	0	-0.035	0.000	0.00	-0.15	0.15	-0.004
12	-1.224	-1.552	-1.07	-2.99	-0.77	-1.04	-1.435	-0.424	-1.35	-2.99	-0.42	-1.312
13	-2.487	-2.854	-2.59	-4.12	-2.66	-2.5	-2.720	-2.364	-2.62	-4.12	-2.36	-2.787
14	-2.958	-3.398	-3.23	-4.25	-3.58	-3.09	-3.156	-2.759	-3.09	-4.25	-2.76	-3.301
15	-2.631	-3.116	-2.83	-3.31	-3.53	-2.64	-2.844	-2.431	-2.76	-3.53	-2.43	-2.915
16	-1.349	-1.820	-1.55	-1.44	-2.44	-1.35	-1.716	-1.140	-1.56	-2.44	-1.14	-1.600
17	0.000	0.000	0	0	-0.36	0	0.000	0.000	0.00	-0.36	0	-0.045
18	0.950	0.775	0.8	1.76	0.24	0.88	0.773	1.292	0.61	0.24	1.76	0.934
19	2.378	2.232	2.34	3.38	1.53	2.33	2.301	2.445	2.10	1.53	3.38	2.367
20	2.866	2.933	2.99	3.68	2.32	2.95	2.967	2.941	2.74	2.32	3.68	2.955
21	3.213	3.323	3.37	3.82	2.64	3.31	3.278	3.405	3.05	2.64	3.82	3.294
22	3.285	3.487	3.53	3.82	2.90	3.35	3.461	3.594	3.23	2.9	3.82	3.429
23	3.331	3.514	3.61	3.79	3.02	3.49	3.500	3.696	3.31	3.02	3.79	3.493
24	3.388	3.561	3.66	3.78	3.01	3.53	3.472	3.769	3.36	3.01	3.78	3.521

HOURLY HEATING & COOLING LOAD DATA
CASE 900 JAN 4
[USE (-) FOR COOLING]
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX
HOUR	kWh	kWh	kWh	kWh	kWh	kWh	kWh	kWh
1	3.104	3.1	3.39	3.74	2.44	3.21	3.081	3.400	2.94	2.44	3.74	3.183
2	3.199	3.24	3.54	3.90	2.61	3.35	3.203	3.547	3.09	2.61	3.9	3.322
3	3.204	3.28	3.56	3.91	2.62	3.38	3.278	3.573	3.17	2.62	3.91	3.351
4	3.306	3.38	3.61	3.97	2.67	3.45	3.331	3.629	3.22	2.67	3.97	3.417
5	3.367	3.45	3.67	4.01	2.74	3.51	3.417	3.687	3.28	2.74	4.01	3.480
6	3.399	3.5	3.72	4.05	2.80	3.56	3.469	3.747	3.34	2.8	4.05	3.530
7	3.453	3.56	3.76	4.08	2.83	3.61	3.517	3.797	3.38	2.83	4.08	3.575
8	3.376	3.52	3.75	4.02	2.84	3.61	3.464	3.794	3.34	2.84	4.02	3.545
9	2.898	2.97	3.17	3.09	2.64	3.08	2.833	3.168	2.80	2.64	3.17	2.982
10	2.346	2.2	2.32	1.81	2.12	2.35	2.056	2.449	2.10	1.81	2.45	2.206
11	1.398	1.03	0.95	0.11	1.50	1.12	0.793	1.293	0.84	0.11	1.5	1.024
12	0.377	0.23	0.1	0	0.68	0.3	0.037	0.619	0.00	0	0.68	0.293
13	0.000	0	0	0	0.07	0	0.000	0.136	0.00	0	0.14	0.026
14	0.000	0	0	0	0	0	0.000	0.000	0.00	0	0	0.000
15	0.000	0	0	0	0	0	0.000	0.000	0.00	0	0	0.000
16	0.000	0	0	0	0	0	0.000	0.088	0.00	0	0.09	0.011
17	0.124	0	0.28	0	0.03	0.14	0.135	1.198	0.00	0	1.2	0.238
18	0.767	0.74	1.22	0	0.41	0.91	0.764	1.602	0.69	0	1.6	0.801
19	1.306	1.14	1.61	0.26	0.80	1.28	1.199	1.805	1.13	0.26	1.81	1.175
20	1.613	1.43	1.82	1.00	1.07	1.54	1.459	1.943	1.41	1	1.94	1.483
21	1.926	1.7	2.04	1.57	1.27	1.81	1.701	2.121	1.63	1.27	2.12	1.767
22	2.136	1.89	2.17	1.96	1.50	2	1.934	2.227	1.83	1.5	2.23	1.978
23	2.221	2.03	2.29	2.27	1.66	2.15	2.092	2.338	1.99	1.66	2.34	2.132
24	2.311	2.19	2.42	2.55	1.75	2.31	2.227	2.458	2.14	1.75	2.55	2.277

FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
CODENAME:	BLAST	DOE2.1D	SUNCODE	SERI-RES	ESP	S3PAS	VUB/BRE	TASE	Popolo	RANGE	RANGE	Average
COUNTRY:	US/ITALY	USA	USA	UK	UK-DMU	SPAIN	Belgium/UK	FINLAND		MIN	MAX
TEMP (C)	# HOURS	# HOURS	# HOURS	# HOURS	# HOURS	# HOURS	# HOURS	# HOURS
-50	0	0	0	0	0	0	0	0	0	0	0	0
-49	0	0	0	0	0	0	0	0	0	0	0	0
-48	0	0	0	0	0	0	0	0	0	0	0	0
-47	0	0	0	0	0	0	0	0	0	0	0	0
-46	0	0	0	0	0	0	0	0	0	0	0	0
-45	0	0	0	0	0	0	0	0	0	0	0	0
-44	0	0	0	0	0	0	0	0	0	0	0	0
-43	0	0	0	0	0	0	0	0	0	0	0	0
-42	0	0	0	0	0	0	0	0	0	0	0	0
-41	0	0	0	0	0	0	0	0	0	0	0	0
-40	0	0	0	0	0	0	0	0	0	0	0	0
-39	0	0	0	0	0	0	0	0	0	0	0	0
-38	0	0	0	0	0	0	0	0	0	0	0	0
-37	0	0	0	0	0	0	0	0	0	0	0	0
-36	0	0	0	0	0	0	0	0	0	0	0	0
-35	0	0	0	0	0	0	0	0	0	0	0	0
-34	0	0	0	0	0	0	0	0	0	0	0	0
-33	0	0	0	0	0	0	0	0	0	0	0	0
-32	0	0	0	0	0	0	0	0	0	0	0	0
-31	0	0	0	0	0	0	0	0	0	0	0	0
-30	0	0	0	0	0	0	0	0	0	0	0	0
-29	0	0	0	0	0	0	0	0	0	0	0	0
-28	0	0	0	0	0	0	0	0	0	0	0	0
-27	0	0	0	0	0	0	0	0	0	0	0	0
-26	0	0	0	0	0	0	0	0	0	0	0	0
-25	0	0	0	0	0	0	0	0	0	0	0	0
-24	0	0	0	0	0	0	0	0	0	0	0	0
-23	0	0	0	0	0	0	0	0	0	0	0	0
-22	0	0	0	0	0	0	0	0	0	0	0	0
-21	0	0	0	0	0	0	0	0	0	0	0	0
-20	0	0	0	0	0	0	0	0	0	0	0	0
-19	0	0	0	0	0	0	0	0	0	0	0	0
-18	0	0	0	0	0	0	0	0	0	0	0	0
-17	0	0	0	0	0	0	0	0	0	0	0	0
-16	0	0	0	0	0	0	0	0	0	0	0	0
-15	0	0	0	0	0	0	0	0	0	0	0	0
-14	0	0	0	0	0	0	0	0	0	0	0	0
-13	0	0	0	0	0	0	0	0	0	0	0	0
-12	0	0	0	0	0	0	0	0	0	0	0	0
-11	0	0	0	0	0	0	0	0	0	0	0	0
-10	0	0	0	0	0	0	0	0	0	0	0	0
-9	0	0	0	0	0	0	0	0	0	0	0	0
-8	0	0	0	0	0	0	0	0	0	0	0	0
-7	0	0	0	0	0	0	1	0	0	0	1	0.13
-6	0	0	0	0	0	0	3	2	0	0	3	0.63
-5	0	1	2	0	0	0	3	4	0	0	4	1.25
-4	1	3	3	4	0	4	6	5	4	0	6	3.25
-3	3	7	5	2	0	3	6	7	2	0	7	4.13
-2	5	5	7	7	3	8	12	10	5	3	12	7.13
-1	6	10	7	5	3	5	13	18	10	3	18	8.38
0	10	18	19	18	8	18	12	20	14	8	20	15.38
1	17	17	19	10	6	20	12	12	13	6	20	14.13
2	14	18	13	20	18	14	20	16	16	13	20	16.63
3	19	19	15	15	18	19	18	25	16	15	25	18.5
4	14	20	23	20	17	21	20	24	19	17	24	19.88
5	25	30	28	24	18	27	26	27	20	18	30	25.63
6	19	25	29	27	22	30	34	35	32	22	35	27.63
7	33	37	28	28	31	33	29	45	31	28	45	33
8	34	51	46	33	30	46	44	59	33	30	59	42.88
9	42	59	62	57	42	61	55	73	61	42	73	56.38
10	54	84	69	53	51	71	57	118	58	51	118	69.63
11	72	107	111	89	67	116	95	134	89	67	134	98.88
12	115	139	137	112	90	127	127	138	117	90	139	123.13
13	137	153	141	142	115	157	143	173	143	115	173	145.13
14	159	158	154	151	156	160	162	183	176	151	183	160.38
15	165	206	188	178	172	207	183	234	172	172	234	191.63
16	198	239	232	195	215	224	234	274	226	195	274	226.38
17	245	274	253	248	244	255	273	298	252	244	298	261.25
18	277	350	301	266	293	315	296	342	283	266	350	305
19	317	322	336	332	338	347	356	352	348	322	356	337.5
20	365	375	342	344	387	352	346	331	360	331	387	355.25
21	358	392	362	361	398	366	388	334	382	334	398	369.88
22	372	364	329	376	385	349	380	343	370	329	385	362.25
23	341	370	348	366	396	357	366	349	360	348	396	361.63
24	368	381	352	341	380	341	401	338	371	338	401	362.75
25	357	432	361	397	417	392	404	404	383	361	432	395.5
26	389	431	373	426	455	399	436	393	426	373	455	412.75
27	420	415	415	418	459	403	465	396	462	396	465	423.88
28	463	452	390	446	445	440	412	411	450	390	452	432.38
29	419	410	405	432	459	396	408	391	442	391	459	415
30	396	404	418	422	415	395	398	362	434	362	422	401.25
31	393	342	401	389	406	360	335	342	394	335	406	371
32	348	349	341	334	369	337	348	322	381	322	369	343.5
33	315	309	330	338	339	306	310	291	333	291	339	317.25
34	321	242	285	311	277	306	297	266	275	242	311	288.13
35	303	197	246	262	230	256	202	210	232	197	262	238.25
36	254	185	213	203	191	217	197	169	183	169	217	203.63
37	195	136	156	189	164	166	161	151	155	136	189	164.75
38	175	92	146	137	108	138	97	132	103	92	146	128.13
39	99	74	112	103	71	97	86	85	72	71	112	90.88
40	66	35	90	71	37	57	48	59	38	35	90	57.88
41	32	16	58	35	15	31	22	32	13	15	58	30.13
42	25	5	36	18	0	10	11	20	1	0	36	15.63
43	5	0	18	5	0	1	2	1	0	0	18	4
44	0	0	5	0	0	0	0	0	0	0	5	0.63
45	0	0	0	0	0	0	0	0	0	0	0	0
46	0	0	0	0	0	0	0	0	0	0	0	0
47	0	0	0	0	0	0	0	0	0	0	0	0
48	0	0	0	0	0	0	0	0	0	0	0	0
49	0	0	0	0	0	0	0	0	0	0	0	0
50	0	0	0	0	0	0	0	0	0	0	0	0
51	0	0	0	0	0	0	0	0	0	0	0	0
52	0	0	0	0	0	0	0	0	0	0	0	0
53	0	0	0	0	0	0	0	0	0	0	0	0
54	0	0	0	0	0	0	0	0	0	0	0	0
55	0	0	0	0	0	0	0	0	0	0	0	0
56	0	0	0	0	0	0	0	0	0	0	0	0
57	0	0	0	0	0	0	0	0	0	0	0	0
58	0	0	0	0	0	0	0	0	0	0	0	0
59	0	0	0	0	0	0	0	0	0	0	0	0
60	0	0	0	0	0	0	0	0	0	0	0	0
61	0	0	0	0	0	0	0	0	0	0	0	0
62	0	0	0	0	0	0	0	0	0	0	0	0
63	0	0	0	0	0	0	0	0	0	0	0	0
64	0	0	0	0	0	0	0	0	0	0	0	0
65	0	0	0	0	0	0	0	0	0	0	0	0
66	0	0	0	0	0	0	0	0	0	0	0	0
67	0	0	0	0	0	0	0	0	0	0	0	0
68	0	0	0	0	0	0	0	0	0	0	0	0
69	0	0	0	0	0	0	0	0	0	0	0	0
70	0	0	0	0	0	0	0	0	0	0	0	0
71	0	0	0	0	0	0	0	0	0	0	0	0
72	0	0	0	0	0	0	0	0	0	0	0	0
73	0	0	0	0	0	0	0	0	0	0	0	0
74	0	0	0	0	0	0	0	0	0	0	0	0
75	0	0	0	0	0	0	0	0	0	0	0	0
76	0	0	0	0	0	0	0	0	0	0	0	0
77	0	0	0	0	0	0	0	0	0	0	0	0
78	0	0	0	0	0	0	0	0	0	0	0	0
79	0	0	0	0	0	0	0	0	0	0	0	0
80	0	0	0	0	0	0	0	0	0	0	0	0
81	0	0	0	0	0	0	0	0	0	0	0	0
82	0	0	0	0	0	0	0	0	0	0	0	0
83	0	0	0	0	0	0	0	0	0	0	0	0
84	0	0	0	0	0	0	0	0	0	0	0	0
85	0	0	0	0	0	0	0	0	0	0	0	0
86	0	0	0	0	0	0	0	0	0	0	0	0
87	0	0	0	0	0	0	0	0	0	0	0	0
88	0	0	0	0	0	0	0	0	0	0	0	0
89	0	0	0	0	0	0	0	0	0	0	0	0
90	0	0	0	0	0	0	0	0	0	0	0	0
91	0	0	0	0	0	0	0	0	0	0	0	0
92	0	0	0	0	0	0	0	0	0	0	0	0
93	0	0	0	0	0	0	0	0	0	0	0	0
94	0	0	0	0	0	0	0	0	0	0	0	0
95	0	0	0	0	0	0	0	0	0	0	0	0
96	0	0	0	0	0	0	0	0	0	0	0	0
97	0	0	0	0	0	0	0	0	0	0	0	0
98	0	0	0	0	0	0	0	0	0	0	0	0

ANNUAL INCIDENT SOLAR RADIATION
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
CASE#	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)
NORTH	427.0		434.0	456.0	407.0	457.0	367.0	453.0	455.1	367.000	457.000	428.714	○	-
EAST	959		1155	1083	1217	1082	1101	962	1080.3	959.000	1217.000	1079.857	○	-
WEST	1086		1079	1003	857	1002	1012	1090	1004.2	857.000	1090.000	1018.429	○	-
SOUTH	1456		1566	1476	1468	1474	1522	1468	1477.7	1456.000	1566.000	1490.000	○	-
HORIZONTAL	1797		1831	1832	1832	1832	1832	1832	1832.6	1797.000	1832.000	1826.857	×	1.8%

ANNUAL TRANSMITTED SOLRAD UNSHADED
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
CASE#	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)
WEST	732.0		735.0	689.0	563.0	642.0	662.0	706.0	730.9	563.000	735.000	675.571	○	-
SOUTH	946		1051	962	954	926	984	914	973.5	914.000	1051.000	962.429	○	-

ANNUAL TRANSMITTED SOLRAD SHADED
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average	Pass	Error Rate
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
CASE#	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)
WEST	599.0		481.0	554.0	441.0	431.0	438.0	469.0	521.0	431.000	599.000	487.571	○	-
SOUTH	785		831	803	775	757	782	809	828.9	757.000	831.000	791.714	○	-

ANNUAL TRANSMISSIVITY COEFFICIENT OF WINDOWS
(UNSHADED TRANSMITTED)/(INCIDENT SOLRAD)
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
CASE#	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)
NORTH	0.674		0.681	0.687	0.657	0.641	0.654	0.648	0.728	0.641	0.687	0.663
EAST	0.650		0.671	0.652	0.650	0.628	0.647	0.623	0.659	0.623	0.671	0.646

ANNUAL OVERHANG AND FIN SHADING COEFFICIENTS
(1-(SHADED)/(UNSHADED)) TRANSMITTED SOLRAD
CODENAME:	ESP	BLAST	DOE2	SRES/SUN	SERIRES	S3PAS	TRNSYS	TASE	Popolo	RANGE	RANGE	Average
COUNTRY:	UK-DMU	USA/ITALY	USA	USA	UK-BRE	SPAIN	BEL/UK	FINLAND		MIN	MAX
CASE#	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)	TMP (C)
NORTH	0.182		0.346	0.196	0.217	0.329	0.338	0.336	0.287	0.182	0.346	0.278
EAST	0.170		0.209	0.165	0.188	0.183	0.205	0.115	0.149	0.115	0.209	0.176