Popolo Reference Manual

Copyright (c) 2010 Eisuke Togashi / Permission is granted to copy, distribute and/or modify this document under the terms of the GNU Free Documentation License, Version 1.2 or any later version published by the Free Software Foundation; with no Invariant Sections, no Front-Cover Texts, and no Back-Cover Texts. A copy of the license is included in the section entitled "GNU Free Documentation License".

# Introduction

## What is Popolo

Popolo is a collection of classes for calculating various heat transfer phenomena. The routines have been written from scratch in C#, and present a modern Applications Programming Interface (API) for .NET Framework programmers, allowing wrappers to be written for very high level languages. It contains classes to calculate solid conduction, convective heat transfer near wall surfaces, air ventilation, radiative heat balance of wall surfaces, transmitted solar radiation through a window, and so on. Users should build up these classes to simulate a whole complex building system. A sample source code to build test cases of BESTEST are provided. Since all the source code is distributed under the GNU General Public License, they can be freely downloaded from the Web site.

This manual describes how to use Popolo in your program. Some example codes are also provided.

## Where to Download Popolo

The latest release of Popolo can be downloaded from website (http://www.hvacsimulator.net). If you extract zipped file, you can find two dll files, Popolo.dll and GSLNET.dll. Popolo.dll is a main file and GSLNET.dll numerical library which is used in Popolo. GSLNET.dll is a wrapper library for GSL (GNU Scientific Library).

## Making the first simple program

In order to use a “Popolo.dll” in your application, you must first add a reference to it. The procedure to make reference to dll files with Visual Studio 2008 is described below.

Figure 1.1 shows the start up window of Visual Studio. Selecting “File” - “New” - “Project”, you can open “New project” window as shown in Figure 1.2. Select “Visual C#” and “Console Application”, then click “OK” button.†[1])
[1] You may also use some other languages which support .NET Framework such as C++.NET or Basic.NET.

Fig.1.1 Start up window of Visual Studio

Fig.1.2 New Project Window

As shown in figure 1.3, a simple program is automatically generated by Visual Studio. In Solution Explorer, right-click on the project node and click Add Reference. In the Add Reference dialog box (Figure 1.4), select the “Browse” tab to browse for “Popolo.dll” in the file system (Figure 1.5). You can find that the reference to the “Popolo.dll” is added in the Solution Explorer (Figure 1.6).

Fig.1.3 Console application project automatically generated by Visual Studio

Fig.1.4 Add Reference dialog box 1	Fig.1.5 Add Reference dialog box 2

Fig.1.6 Reference to “Popolo.dll”

Popolo.dll includes various types of classes to execute building environmental simulation. They are divided into some name spaces. C# programs are organized using namespaces. “”using” directives are provided to facilitate the use of namespaces.
The following example (Figure 1.7) shows how to define a using directive. In line 3, “Popolo.ThermophysicalProperty” namespace is referenced. It is the namespace that provides classes to calculate thermo-physical property of water or moist air. In line 11, MoistAir class which belongs to “Popolo.ThermophysicalProperty” is called.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16	using System; / using Popolo.ThermophysicalProperty; / namespace ConsoleApplication / { / class Program / { / static void Main(string[] args) / { / double cpAir = MoistAir.GetSpecificHeat(0.018); / Console.WriteLine("Specific heat of moist air at humidity ratio of 0.018 kg/kg(DA) is" + cpAir.ToString(“F3”) + "kJ/K"); / Console.Read(); / } / } / }

Fig.1.7 Sample program using “Popolo.ThermophysicalProperty” namespace

Either by hitting F5 key or choosing "Start Debugging" from the menu, the executable will start. Figure 1.8 is the result of the program. You can find that the specific heat of moist air is successfully calculated

Fig.1.8 The result of the first sample program

# Calculating Thermodynamic Properties

## Name space for calculating thermodynamic properties

The classes which calculate a thermodynamic properties belong to “Popolo.ThermophysicalProperty” namespace. Table 2.1 shows principal members defined in “Popolo.ThermophysicalProperty” namespace.

Table 2.1 Principal members defined in “Popolo.ThermophysicalProperty” namespace
Name	Type	General function
MoistAir	class	A class which express the moist air. The functions which calculates thermodynamic properties of the moist air is also defined in this class.
ImmutableMoistAir	interface	Read only interface for MoistAir class.
Water	static class	The functions which calculates thermodynamic properties of the water is defined in this class.

## Calculating thermodynamic properties of moist air

The MoistAir class can be used to calculate thermodynamic properties of the moist air. Most of functions are transported from HVACSIM[1]). and some of the functions are based on the Udagawa's program[2]).
[1] Daniel R. Clark : HVACSIM building systems and equipment simulation program reference manual
[2] 宇田川光弘 : パソコンによる空気調和計算法, オーム社, 1986

### The members of the MoistAir class

There are 7 primary variables which characterize a moist air, “Drybulb temperature”, “Wetbulb temperature”, “Enthalpy”, “Relative humidity”, “Humidity ratio”, “Specific volume” and “Atmospheric pressure”. These variables are defined as properties of the MoistAir class as shown in the table 2.2.

Table 2.2 Properties of the MoistAir class
Name	Mean	Has set accessor	Unit	Type
DryBulbTemperature	Drybulb temperature	yes	°C	double
WetBulbTemperature	Wetbulb temperature	yes	°C	double
Enthalpy	Enthalpy	yes	kJ/kg	double
RelativeHumidity	Relative humidity	yes	%	double
HumidityRatio	Humidity ratio	yes	kg/kg(DA)	double
SpecificVolume	Specific volume	yes	m3/kg	double
AtmosphericPressure	Atmospheric pressure	yes	kPa	double

Figure 2.1 is the sample code which edits the values of the properties of MoistAir object. In the line 11, an instance of the MoistAir class is created. From line 13 to line 20, values are set to the properties. From line 22 to line 29, the values of the MoistAir object is written to the standard output stream.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34	using System; / using Popolo.ThermophysicalProperty; / namespace ConsoleApplication / { / class Program / { / static void Main(string[] args) / { / //Creating instance of MoistAir class / MoistAir mAir = new MoistAir(); / //Set values to property / mAir.DryBulbTemperature = 25.6; / mAir.HumidityRatio = 0.018; / mAir.RelativeHumidity = 50.0; / mAir.WetBulbTemperature = 22; / mAir.SpecificVolume = 0.86; / mAir.Enthalpy = 58.0; / mAir.AtmosphericPressure = 101.325; / //Output values of properties / Console.WriteLine("Drybulb Temperature:" + mAir.DryBulbTemperature); / Console.WriteLine("Humidity Ratio:" + mAir.HumidityRatio); / Console.WriteLine("Relative Humidity:" + mAir.RelativeHumidity); / Console.WriteLine("Wetbulb Temperature:" + mAir.WetBulbTemperature); / Console.WriteLine("Specific Volume:" + mAir.SpecificVolume); / Console.WriteLine("Enthalpy:" + mAir.Enthalpy); / Console.WriteLine("Atmospheric Pressure:" + mAir.AtmosphericPressure); / Console.Read(); / } / } / }

Fig.2.1 The sample code to edit the values of the MoistAir property

Figure 2.2 shows the result of the sample code 2.1.

Fig.2.2 Result of the sample code 2.1

### How to calculate thermodynamic properties of the moist air

An enumeration type “Property” which expresses the moist air properties is defined in MoistAir class. Table 2.3 shows a list of MoistAir.Property enumerator.
For each atmospheric pressure, two known properties allow determination of all other properties of the moist air. To calculate thermodynamic properties from two known properties, user can use static methods shown in table 2.4. The static methods are named as “GetAirStateFromXXYY”, where XX and YY represent two known properties. DB is Dry-Bulb temperature, HR is Humidity Ratio, RH is Relative Humidity, EN is ENthalpy, WB is Wet-Bulb temperature, SV is Specific Volume.

Table 2.3 A list of MoistAir.Property enumerator
Name	Meaning
DryBulbTemperature	Drybulb Temperature[°C]
WetBulbTemperature	Wetbulb Temperature [°C]
HumidityRatio	Humidity Ratio [kg/kg(DA)]
RelativeHumidity	Relative Humidity [%]
Enthalpy	Enthalpy [kJ/kg]
WaterPartialPressure	Water Partial Pressure [kPa]
SpecificVolume	Specific Volume [m3/kg]
SaturatedTemperature	Saturated Temperature [°C]

Table 2.4 Static methods to calculate thermodynamic properties of the moist air
Name	General function
GetAirStateFromAHEN	Calculate thermodynamic properties from humidity ratio [kg/kg] and enthalpy [kJ/kg]
GetAirStateFromAHRH	Calculate thermodynamic properties from humidity ratio [kg/kg] and relative humidity [%]
GetAirStateFromAHSV	Calculate thermodynamic properties from humidity ratio [kg/kg] and specific volume [m3/kg]
GetAirStateFromDBAH	Calculate thermodynamic properties from dry bulb temperature [°C] and humidity ratio [kg/kg]
GetAirStateFromDBEN	Calculate thermodynamic properties from dry bulb temperature [°C] and enthalpy [kJ/kg]
GetAirStateFromDBRH	Calculate thermodynamic properties from dry bulb temperature [°C] and relative humidity [%]
GetAirStateFromDBSV	Calculate thermodynamic properties from dry bulb temperature [°C] and specific volume [m3/kg]
GetAirStateFromDBWB	Calculate thermodynamic properties from dry bulb temperature [°C] and wet bulb temperature [°C]
GetAirStateFromRHEN	Calculate thermodynamic properties from relative humidity [%] and enthalpy [kJ/kg]
GetAirStateFromRHSV	Calculate thermodynamic properties from relative humidity [%] and specific volume [m3/kg]
GetAirStateFromWBAH	Calculate thermodynamic properties from wet bulb temperature [°C] and humidity ratio [kg/kg]
GetAirStateFromWBEN	Calculate thermodynamic properties from wet bulb temperature [°C] and enthalpy [kJ/kg]
GetAirStateFromWBRH	Calculate thermodynamic properties from wet bulb temperature [°C] and relative humidity [%]
GetAirStateFromWBSV	Calculate thermodynamic properties from wet bulb temperature [°C] and specific volume [m3/kg]

Each method is over loaded and have 4 combinations of parameters. Table 2.5 shows return value and 4 combinations of parameters.
The first and the second method calculates all the thermodynamic properties of the moist air from given two state. It returns MoistAir object whose Properties are correctly set upped. The second method request a value of atmospheric pressure as third parameter. By contrast, the first method suppose the value of the atmospheric pressure as 101.325 kPa.
The third and the fourth method calculates value of only one specific property of the moist air. They need shorter calculating time than the first and the second method.

Table 2.5 Return value and 4 combinations of parameters
No.	Return value	param 1	param 2	param 3	param 4
1	MoistAir object	value of specific property 1	value of specific property 2	N/A	N/A
2	MoistAir object	value of specific property 1	value of specific property 2	atmospheric pressure [kPa]	N/A
3	value of specific property (double)	value of specific property 1	value of specific property 2	MoistAir.Property	N/A
4	value of specific property (double)	value of specific property 1	value of specific property 2	MoistAir.Property	atmospheric pressure [kPa]

Figure 2.3 shows the sample code which calculates the values of the properties of MoistAir. In the line 14, using “GetAirStateFromDBHR” method, state of the moist air is calculated from the value of dry bulb temperature and humidity ratio. The value of the moist air are written to the standard output stream. In the line 27, “MoistAir.Property” enumerator is given as third parameter of the GetAirStateFromDBEN method. Therefore, only the value of humidity ratio is calculated.
Figure 2.4 shows the result.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33	using System; / using Popolo.ThermophysicalProperty; / namespace ConsoleApplication / { / class Program / { / static void Main(string[] args) / { / //Create an instance of the MoistAIr class / MoistAir mAir; / //Calculate state of the moist air from given two properties (DB 25 °C, AH 0.012 kg/kg) / mAir = MoistAir.GetAirStateFromDBAH(25, 0.012); / //Write value of the moist air to standard output stream. / Console.WriteLine("Dry bulb temperature:" + mAir.DryBulbTemperature.ToString("F1")); / Console.WriteLine("Humidity ratio:" + mAir.HumidityRatio.ToString("F3")); / Console.WriteLine("Relative humidity:" + mAir.RelativeHumidity.ToString("F1")); / Console.WriteLine("Wet bulb temperature:" + mAir.WetBulbTemperature.ToString("F1")); / Console.WriteLine("Specific volume:" + mAir.SpecificVolume.ToString("F3")); / Console.WriteLine("Enthalpy:" + mAir.Enthalpy.ToString("F1")); / Console.WriteLine("Atmospheric pressure:" + mAir.AtmosphericPressure.ToString("F1")); / Console.WriteLine(); / //Calculate relative humidity from dry bulb temperature and enthalpy. / double rHumid = MoistAir.GetAirStateFromDBEN(25, 58, MoistAir.Property.RelativeHumidity); / Console.WriteLine("Relative Humidity:" + rHumid.ToString("F1")); / Console.Read(); / } / } / }

Fig.2.3 The sample code calculating the values of the properties of moist air

Fig.2.4 Result of the sample code

### Calculation of saturated moist air

Table 2.6 shows the lists of static method to calculate saturated moist air state. They take two or three arguments. The first argument is value of a specific property of the moist air (ex. dry-bulb temperature, humidity ratio). The second argument is “MoistAir.Property”, the enumerating object. The third object is value of atmospheric pressure.

Table 2.6 The lists of static method to calculate saturated moist air state
Name	General function
GetSaturatedDrybulbTemperature	Calculate saturated dry-bulb temperature from one of value of moist air property.
GetSaturatedHumidityRatio	Calculate saturated humidity ratio from one of value of moist air property.
GetSaturatedEnthalpy	Calculate saturated enthalpy from one of value of moist air property.
GetSaturatedVaporPressure	Calculate saturated vapor pressure from one of value of moist air property.

### Immutable interface for MoistAir class

As described above, MoistAir object has double type properties which contains values of the moist air states (ex. dry-bulb temperature, humidity ratio). Therefore, MoistAir object could be an argument or return value of some other method. For example, when we calculate an air handling unit, a cooling coil need state of inlet moist air which is outlet state of a fan. In this case, a MoistAir object will be given from a Fan object to a CoolingCoil object. Since the cooling coil has no ability to alter the value of inlet moist air state, the access for properties of MoistAir objects should be denied from the CoolingCoil object.
To enable this access control, ImmutableMoistAir interface is provided. ImmutableMoistAir interface has exactly same properties as MoistAir class, but only get accessors are defined. Therefore, we can't set values to ImmutableMoistAir properties. They are read-only properties. MoistAir object can be treated as ImmutableMoistAir object, since it implements ImmutableMoistAir interface. Figure 2.5 is the UML diagrams.

Fig.2.5 UML diagram of MoistAir class and ImmutableMoistAir interface

Figure 2.6 is a sample code which uses ImmutableMoistAir interface.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23	using System; / using Popolo.ThermophysicalProperty; / namespace ConsoleApplication / { / class Program / { / static void Main(string[] args) / { / //Create an instance of ImmutableMoistAir / ImmutableMoistAir mAir; / //Create MoistAir object and set it to ImmutableMoistAir object / mAir = MoistAir.GetAirStateFromDBAH(25, 0.012); / //Compile error occurs since ImmutableMoistAir interface doesn't have set accessors / //mAir.DryBulbTemperature = 27; / //mAir.Enthalpy = 56; / } / } / }

Fig. 2.6 Sample code which uses ImmutableMoistAir interface.

### Other methods defined in MoistAIr class

#### BlendAir method

To calculate blended moist air state, BlendAir method is defined. Table 2.7 shows arguments of BlendAir method. Figure 2.7 is a sample code which uses BlendAir method. It creates two ImmutableMoistAir objects and blend them (mixing ratio is 3:7).

Table 2.7 Arguments of BlendAir method
No.	Argument 1	Argument 2	Argument 3	Argument 4
1	Blended moist air 1 / (ImmutableMoistAir)	Blended moist air 2 / (ImmutableMoistAir)	Blend rate of moist air 1 / (double)	Blend rate of moist air 2 / (double)
2	List of blended moist air / (ImmutableMoistAir[ ])	Blend rate of moist air / (double[ ])	-	-
3	Dry-bulb temperature list of blended moist air / (double[ ])	Humidity raiot list of blended moist air / (double[ ])	-	-

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30	using System; / using Popolo.ThermophysicalProperty; / namespace ConsoleApplication / { / class Program / { / static void Main(string[] args) / { / //Create an instance of MoistAir class / ImmutableMoistAir mAir1, mAir2, blendAir; / //Calculate moist air state (DB 25C, AH 0.012kg/kgDA) / mAir1 = MoistAir.GetAirStateFromDBAH(25, 0.012); / //Calculate moist air state (DB 30C, AH 0.014kg/kgDA) / mAir2 = MoistAir.GetAirStateFromDBAH(30, 0.014); / //Blend moist air. (Blend rate is 3:7) / blendAir = MoistAir.BlendAir(mAir1, mAir2, 0.3, 0.7); / Console.WriteLine("Dry bulb temperature:" + blendAir.DryBulbTemperature); / Console.WriteLine("Humidty ratio:" + blendAir.HumidityRatio); / Console.WriteLine("Relative humidity:" + blendAir.RelativeHumidity); / Console.WriteLine("Wet bulb temperature:" + blendAir.WetBulbTemperature); / Console.WriteLine("Specific volume:" + blendAir.SpecificVolume); / Console.WriteLine("Enthalpy:" + blendAir.Enthalpy); / } / } / }

Fig. 2.7 Sample code which uses BlendAir method

#### GetDynamicViscosity method

Method to calculate dynamic viscosity [m2/s] of moist air. An argument is dry bulb temperature.

#### GetSpecificHeat method

Method to calculate specific heat [kJ/(kg K)] of moist air. An argument is humidity ratio.

#### GetThermalConductivity method

Method to calculate thermal conductivity [W/(m K)] of moist air. An argument is dry bulb temperature.

#### GetWaterVaporPressure method

Method to calculate water vapor pressure [kPa] of moist air. An argument is humidity ratio (and atmospheric pressure).
# Calculating Circuit Network

## Name space for calculating circuit network

The classes which calculate a circuit network belong to “Popolo.CircuitNetwork” namespace. Table 3.1 shows principal members defined in “Popolo.CircuitNetwork” namespace.

Table 3.1 Principal members defined in “Popolo.CircuitNetwork” namespace
Name	Type	General function
Channel	class	A class which expresses a channel.
Circuit	class	A class which expresses a circuit. It consists of Channel and Node object.
CircuitSolver	class	A class which solve a Circuit object.
ImmutableChannel	interface	Read only interface for Channel class.
ImmutableCircuit	interface	Read only interface for Circuit class.
ImmutableNode	interface	Read only interface for Node class.
Node	class	A class which expresses a node.

A potential at each node in circuit network can be expressed in equation 3.1[3]). To solve a circuit network, user should make a Circuit object with a Channel and a Node object, which expresses equation 3.1. Then, solve the Circuit object with a CircuitSolver object.
[3] Hiroyasu Okuyama : Bouilding Heat and Air Transfer Models Based on System Theory, Bulletin of the Japan Society for Industrial and Applied Mathematics, 13(1), pp.61-71, 2003

m cdot {dp over dt} = sum from i=0 to N {1 over R_i cdot (p_i - p)^{1 over %eta}} + G	(3.1)

    m : Capacity of node p : Potential of node N : Number of nodes which are connected to target node
    Ri : Resistance between nodes G : Energy flow from the outside to node η : resistive index (1 ≤ η ≤ 2)

## General descriptions of classes in CircuitNetwork namespace

### Node class

Node is a class which expresses a node. A principal parameters of node are potential and capacity. A variable p and m in equation 3.1 represent potential and capacity. If the capacity is very small, value of the potential changes rapidly with the energy flow. User can initialize these value in constructor. For example, to make Node object whose capacity and potential are 5 and 10, user should write code like below. The first argument is a name of the node, the second is value of the capacity, and the third is value of the potential.

Node sampleNode = new Node("SampleNode", 5, 10)

To get the list of the channels which are connected to the node, use GetChannels method. To get the total energy flow to node, use GetTotalFlow method. If the returned value of GetTotalFlow method is less than 0, energy flows to outside of the node.

If the node is the boundary node (the node whose potential should be kept constant value), set value of the IsBoundaryNode property to true. To make constant energy flow to the node, set the energy flow to the ExternalFlow property. If the ExternalFlow is positive value, it means that energy flows from node to outside. If negative, energy flows from outside to node. A variable G in equation 3.1 represent the ExternalFlow.

These properties are used when user make boundary condition. Fig.3.1 shows how to set the boundary conditions.

Figure 3.1 How to set the boundary conditions

As same as the MoistAir class, an immutable interface (ImmutableNode) for the Node class is defined. The Node class implements the ImmutableNode interface.

### Channel class

Channel is a class which expresses a channel. It connects two node objects and represent their connection weight with resistance and resistive index. A variable R and η in equation 3.1 represent resistance and resistive index. User can initialize these value in constructor. For example, to make Channel object whose resistance and resistive index are 3 and 1.2, user should write code like below. The first argument is a name of the channel, the second is value of the resistance, and the third is value of the resistive index.

Channel sampleChannel = new Channel("SampleChannel", 3, 1.2);

To connect two nodes with Channel object, use Connect method.

sampleChannel.Connect(node1, node2);

The first and the second arguments are Node objects to connect.
To get the energy flow in the channel, use GetFlow method. Figure 3.2 is a sample program which calculate energy flow between two nodes. The potential of the first and the second node are 10 and 0. The resistance and resistive index of channel are 2 and 1.2. Energy flow of this channel is 1 / 2 × (10 – 0)(1/1.2) = 3.4.

As same as the Node class, an immutable interface (ImmutableChannel) for the Channel class is defined. The Channel class implements the ImmutableChannel interface.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18	/// <summary>Circuit test 1</summary> / /// <remarks>Calculating energy flow between two nodes</remarks> / private static void circuitTest1() / { / //Create new instance of Node class. / Node node1 = new Node("SampleNode1", 0, 10); / Node node2 = new Node("SampleNode2", 0, 0); / //Create new instance of Channel class and connect nodes. / Channel channel = new Channel("SampleChannel", 2, 1.2); / channel.Connect(node1, node2); / //Calculate energy flow. / double flow = channel.GetFlow(); / Console.WriteLine("Energy flow is : " + flow.ToString("F2")); / Console.Read(); / }

Fig.3.2 A sample program which calculate energy flow between two nodes

### Circuit class

A circuit consists of nodes and channels. To define the circuit, Add Node objects to Circuit object and connect them with Channel objects. To add Node objects to a Circuit object, use AddNode method.

ImmutableNode iNode = sampleCircuit.AddNode(sampleNode);

The return value of AddNode method is the ImmutableNode object which was added to the Circuit object by AddNode method. To remove Node objects from a Circuit object, use RemoveNode method.

sampleCircuit.RemoveNode(iNode);

The first argument is the removing ImmutableNode object.
To connect nodes, use ConnectNodes method.

ImmutableChannel iChannel = sampleCircuit.ConnectNodes(iNode1, iNode2, sampleChannel);

The first and the second arguments are ImmutableNode objects, and the third argument is a Channel object which connects two nodes. The two nodes should be added before calling ConnectNodes method. The returned value of ConnectNodes method is the ImmutableChannel object which connects two nodes.
To disconnect nodes, use DisconnectNodes method.

sampleCircuit.DisconnectNodes(iChannel);

The first argument is the Channel object which connects nodes.

The boundary conditions described at section 3.2.1 could be also set in Circuit class. Table 3.2 shows lists of the method to set boundary conditions which defined in Circuit class.

Table 3.2 The method to set boundary conditions
Name	Function	Argument 1	Argument 2
SetPotential	Set initial value of potential to node	Value of the potential (double)	Target node (ImmutableNode)
SetExternalFlow	Set energy flow from node to outside	Value of the energy flow (double)	Target node (ImmutableNode)
SetBoundaryNode	Set whether node is boundary node or not.	Whether node is boundary node or not (bool)	Target node (ImmutableNode)

### CircuitSolver class

The CircuitSolver class has a function to solve a circuit network. It takes a Circuit object as an argument of constructor.

CircuitSolver cSolver = new CircuitSolver(sampleCircuit);

To solve a circuit network, use Solve method.

cSolver.Solve();

All the value of energy flows and potentials are updated when the Solve method is called. There are two kinds of circuit network, circuit network who has a capacity or not. The capacity is a variable m in equation 3.1. If all the capacities in a network are equal to 0, the network is a static network. In contrast, a network whose capacities takes positive value, is a dynamic network. If a network is a static network, the value of potentials or energy flows will not change unless boundary conditions change. If a network is a dynamic network, the value of potentials or energy flows depends on time. Therefore, user should set time step when a network is a dynamic network. To set time step, use TimeStep property as below. In this case, time step is set to 10 seconds.

cSolver.TimeStep = 10;
## Sample programs calculating circuit networks

In this section, two sample programs which calculate circuit networks are given. One is a static network which represent a water pipe network. The other is a dynamic network which represent heat flow through a wall.

### Calculating a water pipe network

Figure 3.3 shows a water pipe network to solve†[1]). The network has three nodes (1, 2 and 3) and four channels (A, B, C and D). The resistance of each channel are shown in figure (RA ~ RD).
[1] 本問題の手計算による解法については建築設備基礎（著 木村建一）を参照して下さい。

Fig.3.3 A water pipe network to solve

Figure 3.4 is a sample program which solve this network.
New instance of Circuit class is created in the line 5. Three nodes are added in the line 8~10. Since the capacities of these nodes are 0, this network is a static network. The node 1 and the node 2 is connected to outside and water flow rate is 7.06. This external water flow is set in the line 12 and 13.
The channels are created in the line 16 to 19. Since this is a water network, value of the resistive index is 2. In line 22 to 25, the nodes are connected by the channels.
In the line 29, created water flow network is solved by CircuitSolver object. All the potentials and water flow are calculated and written to the standard output stream. Figure 3.5 shows the result of the program.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35	/// <summary>Circuit test 2</summary> / /// <remarks>Calculating water pipe network</remarks> / private static void circuitTest2() / { / Circuit circuit = new Circuit("Circuit network of water pipe"); / //Add nodes to circuit network / ImmutableNode node1 = circuit.AddNode(new Node("1", 0, 0)); / ImmutableNode node2 = circuit.AddNode(new Node("2", 0, 0)); / ImmutableNode node3 = circuit.AddNode(new Node("3", 0, 0)); / //Set external water flow / circuit.SetExternalFlow(-7.06, node1); / circuit.SetExternalFlow(7.06, node3); / //Create channels / Channel chA = new Channel("A", 167, 2); / Channel chB = new Channel("B", 192, 2); / Channel chC = new Channel("C", 840, 2); / Channel chD = new Channel("D", 4950, 2); / //Connect nodes with channels / ImmutableChannel channelA = circuit.ConnectNodes(node1, node3, chA); / ImmutableChannel channelB = circuit.ConnectNodes(node1, node2, chB); / ImmutableChannel channelC = circuit.ConnectNodes(node2, node3, chC); / ImmutableChannel channelD = circuit.ConnectNodes(node2, node3, chD); / //Create solver / CircuitSolver cSolver = new CircuitSolver(circuit); / cSolver.Solve(); / Console.WriteLine("Water flow A is " + channelA.GetFlow().ToString("F2")); / Console.WriteLine("Water flow B is " + channelB.GetFlow().ToString("F2")); / Console.WriteLine("Water flow C is " + channelC.GetFlow().ToString("F2")); / Console.WriteLine("Water flow D is " + channelD.GetFlow().ToString("F2")); / Console.Read(); / }

Fig.3.4 A sample program which solve the water flow network

Fig.3.5 The result of the sample program

### Calculating heat flow through a wall

Figure 3.6 is a wall to calculate a heat transfer. The wall has four layers; plywood, concrete, air gap and rock wool. The temperatures of Room 1 and Room 2 take constant value 20°C and 10°C. The temperatures of each layer are treated as potentials of node in this case.

Fig. 3.6 A wall to calculate a heat transfer

Figure 3.7 is a sample program which solve the heat transfer of this wall.
In the line 8 to 14, new instances of Node class are created. In this case, each nodes has heat capacity. Since the room temperatures take constant value, edge nodes is set to boundary nodes in line 17 and 18.
As same as water pipe network, a CircuitSolver object is used to solve the network. In this case, time step should be set since the network has heat capacity and is a dynamic network. In the line 32, TimeStep is set to 3600 seconds (= 1 hour). Update method is called 24 times. The temperatures (potentials) of layers are written to the standard output stream in each iteration.
Figure 3.8 is a wall temperature distribution made from the result of the program.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40 / 41 / 42 / 43 / 44	/// <summary>Circuit test 3</summary> / /// <remarks>Calculating heat transfer through a wall</remarks> / private static void circuitTest3() / { / Circuit circuit = new Circuit("Heat transfer network through wall"); / //Add nodes to circuit network / ImmutableNode[] nodes = new ImmutableNode[6]; / nodes[0] = circuit.AddNode(new Node("Room 1", 0)); / nodes[1] = circuit.AddNode(new Node("Plywood", 17.9)); / nodes[2] = circuit.AddNode(new Node("Concrete", 232)); / nodes[3] = circuit.AddNode(new Node("Air gap", 0)); / nodes[4] = circuit.AddNode(new Node("Rock wool", 4.2)); / nodes[5] = circuit.AddNode(new Node("Room 2", 0)); / //Set boundary conditions (Room air temperatures). / circuit.SetBoundaryNode(true, nodes[0]); / circuit.SetBoundaryNode(true, nodes[5]); / //Set air temperatures. / circuit.SetPotential(20, nodes[0]); / circuit.SetPotential(10, nodes[5]); / for (int i = 1; i < 5; i++) circuit.SetPotential(10, nodes[i]); //Initialize wall temperatures to 10 C. / //Connect nodes. / ImmutableChannel channel01 = circuit.ConnectNodes(nodes[0], nodes[1], new Channel("Room 1-Plywood", 174, 1)); / ImmutableChannel channel12 = circuit.ConnectNodes(nodes[1], nodes[2], new Channel("Plywood-Concrete", 109, 1)); / ImmutableChannel channel34 = circuit.ConnectNodes(nodes[2], nodes[3], new Channel("Concrete-Air gap", 86, 1)); / ImmutableChannel channel45 = circuit.ConnectNodes(nodes[3], nodes[4], new Channel("Air gap-Rock wook", 638, 1)); / ImmutableChannel channel56 = circuit.ConnectNodes(nodes[4], nodes[5], new Channel("Rock wool-Room 2", 703, 1)); / CircuitSolver cSolver = new CircuitSolver(circuit); / cSolver.TimeStep = 3600; / for (int i = 0; i < nodes.Length; i++) Console.Write(nodes[i].Name + " "); / Console.WriteLine(); / for (int i = 0; i < 24; i++) / { / cSolver.Solve(); / Console.Write((i + 1) + "H : "); / for (int j = 0; j < nodes.Length; j++) Console.Write(nodes[j].Potential.ToString("F1") + " "); / Console.WriteLine(); / } / Console.Read(); / }

Fig.3.7 A sample program which solve the heat transfer of the wall.

Fig.3.8 Wall temperature distribution

# Calculating Thermal Comfort

## Name space for calculating thermal comfort

The classes which calculate thermal comfort of human belong to “Popolo.ThermalComfort” name space. Table 4.1 shows principal members defined in “Popolo.ThermalComfort” namespace.

Table 4.1 Principal members defined in “Popolo.ThermalComfort” namespace
Name	Type	General function
PMVCalculator	static class	A static class which calculate PMV value.
SETStarCalculator	static class	A static class which calculate SET* value.
HumanBody	class	A class which expresses a body of human.
BodyPart	class	A class which expresses a part of a human body.

## General descriptions of classes in ThermalComfort name space

### PMVCalculator class

PMV represents the “predicted mean vote” of a large population of people exposed to a certain environment. PPD is the predicted percent of dissatisfied people at each PMV. As PMV changes away from zero in either the positive or negative direction, PPD increases. These indices are proposed by P. O. Fanger.
To calculate value of PMV and PPD, use PMVCalculator class. Table 4.2 shows a list of principal members of PMVCalculator class.

Table 4.2 Principal members of PMVCalculator class
Name	Type	Description
Tasks	enumerator	An enumerator which expresses a kind of work
GetMet	method	Calculate metabolic rate for a task.
GetPMVFromPPD	method	Calculate PMV value from PPD value.
GetPPDFromPMV	method	Calculate PPD value from PMV value.
TryCalculateDryBulbTemperature	method	Calculate dry-bulb temperature from PMV and other thermal conditions.
TryCalculateHeatLossFromBody	method	Calculate heat loss from a human body.
TryCalculatePMV	method	Calculate PMV value from 6 thermal conditions.
TryCalculateRelativeHumidity	method	Calculate relative humidity from PMV and other thermal conditions.

#### Tasks

Tasks is an enumerator which expresses a kind of work. Some typical tasks (rest, office work, sleeping, exercise and so on) exemplified in ASHRAE Standard 55 is defined.

#### GetMet

GetMet method calculates metabolic rate for a task. It takes Tasks object as an argument.

#### GetPMVFromPPD

GetPMVFromPPD method calculates PMV value from PPD value. Since the curve of PPD is bilaterally symmetric as shown in figure 4.1, 2 PMV value corresponds to 1 PPD value. This method calculate positive value. You can get negative value by reversing a sign.

Table 4.1 PMV-PPD curve

#### GetPPDFromPMV

GetPPDFromPMV method calculate PPD value from PMV value. An argument is a value of PMV.

#### TryCalculateDryBulbTemperature

TryCalculateDryBulbTemperature method calculate dry-bulb temperature from PMV value and other thermal conditions. Table 4.3 shows a list of arguments. The arguments 1 to 7 are the inputs. Figure 4.2 shows a sample program which calculate dry-bulb temperature from PMV and other thermal conditions.

Table 4.3 The arguments of TryCalculateDryBulbTemperature method
No.	Description	No.	Description
1	PMV value [-]	5	Clo value [clo]
2	Mean radiant temperature [°C]	6	Metabolic rate [met]
3	Velocity [m/s]	7	External work [met]
4	Relative Humidity [%]	8	Dry-bulb temperature [°C] (Output)

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8	/// <summary>PMV Test</summary> / private static void pmvTest() / { / double dbt; / PMVCalculator.TryCalculateDryBulbTemperature(1.2, 25.6, 50, 0.1, 0.8, 1.2, 0, out dbt); / Console.WriteLine(dbt); / Console.Read(); / }

Fig.4.2 A sample program which calculate dry-bulb temperature from PMV and other thermal conditions

#### TryCalculateHeatLossFromBody

TryCalculateHeatLossFromBody method calculates a heat loss from a body. Table 4.4 shows a list of arguments. The arguments 1 to 7 are the inputs. The PMV value is calculated from heat loss from body.

Table 4.4 The arguments of TryCalculateHeatLossFromBody nethod
No.	Description	No.	Description
1	Dry-bulb temperature [°C]	5	Clo value [clo]
2	Mean radiant temperature [°C]	6	Metabolic rate [met]
3	Velocity [m/s]	7	External work [met]
4	Relative Humidity [%]	8	Heat loss from body [W] (Output)

#### TryCalculatePMV

TryCalculatePMV method calculates PMV value from 6 thermal conditions. Table 4.5 shows a list of arguments. The method is overloaded, and could be called with arguments listed in table 4.6.

Table 4.5 The arguments of TryCalculatePMV methods 1
No.	Description	No.	Description
1	Dry-bulb temperature [°C]	5	Clo value [clo]
2	Mean radiant temperature [°C]	6	Metabolic rate [met]
3	Velocity [m/s]	7	External work [met]
4	Relative Humidity [%]	8	PMV value [-] (Output)

Table 4.6 The arguments of TryCalculatePMV methods 2
No.	Description	No.	Description
1	Metabolic rate [met]	3	Heat loss from body [W]
2	External work [met]

### SETStarCalculator class

The ET* and the SET* (Standard effective temperature) are the predictive index of human response to the thermal environment proposed by Gagge[4]). To calculate the value of ET* and the value SET*, use TryCalculateSET method. Table 4.7 shows a list of arguments. The arguments 1 to 10 are the inputs, and the 11th and 12th arguments are the outputs.
[4] A.P.Gagge et al. : A standard predictive index of human response to the thermal environment, AHRAE Transaction, Vol.93, 1987

Table 4.7 The arguments of the TryCalculateSET methodz
No.	Description	No.	Description
1	Dry-bulb temperature [°C]	7	External work [met]
2	Mean radiant temperature [°C]	8	Atmospheric pressure [kPa]
3	Velocity [m/s]	9	Weight [kg]
4	Relative Humidity [%]	10	Body surface area [m2]
5	Clo value [clo]	11	ET* [-] (Output)
6	Metabolic rate [met]	12	SET* [-] (Output)

### HumanBody class

During the past 50 years of thermal comfort research, PMV and standard new effective temperature SET* have gained support as indoor thermal comfort indices that are still the most widely utilized indices in the field today. Both indices modeled the human body as a uniform heating element and clothing as the uniform heat resistance on human body surface, limiting the application of these indices to fairly uniform condition with few distributions. However, people are often exposed to very non-uniform thermal environments, each human body segment has physiological and geometric characteristic and clothing insulation of each segment is various.
HumanBody class and BodyPart class are developed to calculate human body model proposed by S.Tanabe[5]). It enables detailed consideration of non-uniform conditions is required to assess such environments as car cabins, task air-conditioned spaces and outdoors. The conceptual figure of heat exchange is illustrated in Fig.4.3.
[5] S.Tanabe, K.Kobayashi, J.Nakano, Y.Ozeki et al.. 2002. Evaluation of thermal comfort using combined multi-node thermoregulation (65MN) and radiation models and computational fluid dynamics (CFD). Energy and Buildings. No.34. pp.637-646.

Figure.4.3 The conceptual figure of heat exchange

HumanBody class has two constructors. An instance of HumanBody is initialized to body of standard adult male. The standard man represents the body surface area of 1.87 m2 ;the body weight of 74.43 kg; age of 25; cardiac index at rest of 2.58 L/(min m2); fat percentage of 15 %. These parameters can be initialized when given as an arguments as below.

public HumanBody(double weight, double height, double age, bool isMale,
double cardiacIndexAtRest, double fatPercentage)

To specify the part of the body, Nodes enumerator is defined in HumanBody class. Table 4.8 shows members of the Nodes enumerator.

Table 4.8 The members of the Nodes enumerator
Name	Description	Name	Description
Head	Head	LeftLeg	Left leg
Neck	Neck	LeftFoot	Left foot
Chest	Chest	RightShoulder	Right shoulder
Back	Back	RightArm	Right arm
Pelvis	Pelvis	RightHand	Right hand
LeftShoulder	Left shoulder	RightThigh	Right thigh
LeftArm	Left arm	RightLeg	Right leg
LeftHand	Left hand	RightFoot	Right foot
LeftThigh	Left thigh	-	-

Table 4.9 shows methods defined in HumanBody class. A temperature of whole body can be initialized with InitializeTemperature method. However, the initialization of the body temperatures is not necessary, since they are initialized to steady state at operative temperature of 28.8 °C when the object is instantiated.
The state of the human body can be updated by the Update method. User can give the time step as an argument.
HumanBody object consists of 17 BodyPart objects. The each BodyPart object can be obtained by calling GetBodyPart method. BodyPart object has detailed information of the body (temperatures of the core, muscle, fat and skin, etc.).

Table 4.9 The methods defined in HumanBody class
Name	Description
Update	Function	Update body state.
	Return	-
	Arg.1	Time step [sec]	-	-
InitializeTemperature	Function	Initialize body temperature.
	Return	-
	Arg.1	Temperature to initialize. [°C]	-	-
GetBodyPart	Function	Get part of human body.
	Return	Part of the body (BodyPart object)
	Arg.1	Part of the body (Nodes enum.)	-	-

Table 4.10 shows methods to set the boundary conditions. By giving Nodes enumerating object as an first argument, different boundary condition can be given to different body part (only methods which has *).

Table 4.10 Members of the HumanBody class : Methods to set boundary cnditions
Name	Description
SetCardiacIndex	Function	Set cardiac index [L/(min m2)]
	Arg. 1	Cardiac index[L/(min m2)] (double)	-	-
SetPosture	Function	Set body posture
	Arg. 1	Body posture (BodyPosture type)	-	-
SetWorkLoad	Function	Set external work load [W/m2]
	Arg. 1	External work load[W/m2] (double)	-	-
※SetContactPortionRate	Function	Set contact portion rate [-]
	Arg. 1	Contact portion rate [-] (double)	-	-
SetHeatConductance / ToMaterial	Function	Set heat conductance to external material [W/(m2 K)]
	Arg. 1	Body position to set heat coductance (Nodes type)	Arg. 2	Heat conductance to external material [W/(m2 K)]
※SetDrybulbTemperature	Function	Set dry-bulb temperature [°C] of ambient
	Arg. 1	Dry-bulb temperature [°C] (double)	-	-
※SetRelativeHumidity	Function	Set relative humidity [%] of ambient moist air
	Arg. 1	Relative humidity [%] (double)	-	-
※SetMeanRadiant / Temperature	Function	Set mean radiant temperature [°C] of ambient
	Arg. 1	Mean radiant temperature [°C] (double)	-	-
※SetMaterialTemperature	Function	Set temperature [°C] of the contacted material
	Arg. 1	Temperature [°C] of the contacted material (double)	-	-
※SetClothingIndex	Function	Set clothing index [clo]
	Arg. 1	Clothing index [clo] (double)	-	-
※SetVelocity	Function	Set velocity [m/s] of ambient
	Arg. 1	Velocity [m/s] (double)	-	-

Table 4.11 shows methods to get a state of the human body. These are the methods to get information about whole body. To get detailed information of particular body part, get BodyPart object by GetBodyPart method, and use methods defined in BodyPart class.

Table 4.11 Members of the HumanBody class : Methods to get state of human body
Name	Description
GetBloodFlow	Function	Get blood flow rate [L/h] of whole human body
	Return	Blood flow rate [L/h] (double)
GetSensibleHeatLossFromSkin	Function	Get sensible heat loss [W] from whole human body skin surface
	Return	Sensible heat loss [W] from whole human body skin surface (double)
GetLatentHeatLossFromSkin	Function	Get latent heat loss [W] from whole human body skin surface
	Return	Latent heat loss [W] from whole human body skin surface (double)
GetMetabolicRate	Function	Get metabolic rate [W] of whole human body. It includes basic metabolic rate, external work and shivering
	Return	Metablic rate [W] of human body (double)
GetAverageSkinTemperature	Function	Get average skin temperature [°C] of whole human body.
	Return	Average skin temperature [°C] (double型)

Table 4.12 shows method to get a state of body part. To specify detailed position of body part, use Segments enumerator. Table 4.13 shows members of Segment enumerator.

Table 4.12 The methods defined in BodyPart class
Name	Description
GetSensibleHeatLoss	Description	Calculate sensible heat loss [W] from the skin.
	Return	Sensible heat loss [W] from the skin. (double)
	-	-	-	-
GetHeatCapacity	Description	Get segment heat capacity [Wh/K] of the body part
	Return	Segment heat capacity [W/K] of the body part. (double)
	Arg.1	Segment of the body part (Segments object)	-	-
GetTemperature	Description	Get segment temperature [°C] of the body part
	Return	Segment temperature [°C] of the body part (double)
	Arg.1	Segment of the body part (Segments object)	-	-
GetHeatConductance	Description	Get heat conductance [W/K] between the segments. If the segments are not contacted, 0 is returned.
	Return	Heat conductance [W/K] between the segments.
	Arg.1	Segment 1 (Segments object)	Arg.2	Segment 2 (Segments object)
GetMetabolicRate	Description	Get segment metabolic rate [W] of the body part
	Return	Segment metabolic rate [W] of the body part (double)
	Arg.1	Segment (Segments object)	-	-
GetBloodFlow	Description	Get blood flow [L/h] at segment of the body part
	Return	Blood flow [L/h] segment (double)
	Arg.1	Segment (Segments object)	-	-
GetHeatTransfer	Description	Calculate heat transfer [W] from a segment 1 to a segment 2.
	Return	Heat transfer[W] from a segment 1 to a segment 2 (double)
	Arg.1	Segment 1 (Segments object)	Arg.2	Segment 2 (Segments object)

Table 4.13 The members of Segments enumerator
Name	Description	Name	Description
Core	Core layer	Artery	Artery
Muscle	Muscle layer	SuperficialVein	Superficial vein
Fat	Fat layer	DeepVein	Deep vein
Skin	Skin layer	AVA	AVA blood

Figure 4.4 shows a sample program which calculates thermal state of human body.
In the line 8, HumanBody object is initialized. It is the model of female and the weight, height, age and cardiac index are 70kg, 1.6m, 35, 2.58 L/(min m2) respectively.
In the line 10 to 19, the boundary conditions are given. This is the code to set boundary conditions simultaneously to whole body parts. To set boundary conditions individually to each body part, give BodyParts object as a first argument as line 22. In this case, dry-bulb temperature just around right hand settled at 20 °C.
The state of body is updated in the line 28. The time step is 120 seconds. The elapse of the time is 30 minutes, since the Update method is called 16 times. Of course, the boundary conditions can be changed at each iteration.

In the line 29 and 30, the left and the right shoulder objects are taken out to get information. The temperatures of the core layer and the skin layer is calculated. They are written to the standard output stream.
Figure 4.5 shows the result of the simulation. The body temperature became higher as the time past. Since the dry-bulb temperature around the right hand settled at 20°C, the temperature of the right shoulder was lower than that of the left shoulder.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40	/// <summary>Sample program calculating human body</summary> / private static void humanBodyTest() / { / //This is constructor to make standard human body. / //HumanBody body = new HumanBody(); / //Make human body model : Weight 70kg, Height 1.6m, Age 35, Female, Cardiac index 2.58, Fat 20% / HumanBody body = new HumanBody(70, 1.6, 35, false, 2.58, 20); / //Set clothing index [clo] / body.SetClothingIndex(0); / //Set dry-bulb temperature [C] / body.SetDrybulbTemperature(42); / //Set mean radiant temperature [C] / body.SetMeanRadiantTemperature(42); / //Set velocity [m/s] / body.SetVelocity(1.0); / //Set relative humidity [%] / body.SetRelativeHumidity(50); / //Use Nodes enumarator to set bouncary condition to particular position / body.SetDrybulbTemperature(HumanBody.Nodes.RightHand, 20); / //Updating body state / Console.WriteLine("Time | R.Shoulder C temp | R.Shoulder S temp | L.Shoulder C temp | L.Shoulder S temp"); / for (int i = 0; i < 15; i++) / { / body.Update(120); / ImmutableBodyPart rightShoulder = body.GetBodyPart(HumanBody.Nodes.RightShoulder); / ImmutableBodyPart leftShoulder = body.GetBodyPart(HumanBody.Nodes.LeftShoulder); / Console.Write(((i + 1) * 120) + "sec | "); / Console.Write(rightShoulder.GetTemperature(BodyPart.Segments.Core).ToString("F2") + " | "); / Console.Write(rightShoulder.GetTemperature(BodyPart.Segments.Skin).ToString("F2") + " | "); / Console.Write(leftShoulder.GetTemperature(BodyPart.Segments.Core).ToString("F2") + " | "); / Console.Write(leftShoulder.GetTemperature(BodyPart.Segments.Skin).ToString("F2") + " | "); / Console.WriteLine(); / } / Console.Read(); / }

Figure 4.4 The sample program which calculates thermal state of human body

Time | R.Shoulder C temp | R.Shoulder S temp | L.Shoulder C temp | L.Shoulder S temp / 120sec | 35.89 | 35.70 | 35.89 | 35.74 | / 240sec | 35.91 | 36.07 | 35.92 | 36.17 | / 360sec | 35.93 | 36.20 | 35.96 | 36.35 | / 480sec | 35.96 | 36.21 | 36.02 | 36.38 | / 600sec | 35.99 | 36.17 | 36.07 | 36.36 | / 720sec | 36.02 | 36.13 | 36.12 | 36.32 | / 840sec | 36.05 | 36.10 | 36.17 | 36.28 | / 960sec | 36.08 | 36.08 | 36.22 | 36.26 | / 1080sec | 36.11 | 36.06 | 36.27 | 36.24 | / 1200sec | 36.14 | 36.05 | 36.31 | 36.22 | / 1320sec | 36.17 | 36.04 | 36.35 | 36.21 | / 1440sec | 36.19 | 36.03 | 36.38 | 36.20 | / 1560sec | 36.21 | 36.03 | 36.41 | 36.20 | / 1680sec | 36.24 | 36.03 | 36.44 | 36.19 | / 1800sec | 36.26 | 36.02 | 36.47 | 36.19 |

Figure 4.5 The result of the simulation

# Calculating Weather State

## Name space for calculating weather state

Classes which calculate weather state belong to “Popolo.Weather” name space. Table 5.1 shows principal members defined in “Popolo.Weather” name space.

Table 5.1 Principal members defined in Popolo.Weather name space
Name	Description
Incline	A class which expresses an incline.
Sky	A static class which calculates various weather phenomena.
Sun	A class which expresses sun.
WeatherData	A class which contains weather data.
WeatherDataTable	A class which contains weather data. It consists of WeatherRecord objects.
WeatherRecord	A class which contains weather data. It consists of WeatherData objects.

## Descriptions of classes

### Incline class

To calculates nocturnal radiation or radiation from sun, 3 dimensional positioning between plane and point should be clearly defined. An incline can be defined with horizontal vertical angle. The Incline class takes these 2 value as an arguments of constructor. The constructor of Incline is overloaded, and there are 3 kinds of arguments as shown in Table 5.2.

Table 5.2 The arguments of Incline constructors
No.	Argument 1	Argument 2
1	Horizontal angle : Unit is radian. South is 0, west is negative, east is positive. / (double)	Vertical angle : Unit is radian. Horizontal surface is 0, Vertical surface is 1/2π / (double)
2	Orientation / (Orientation object)	Vertical angle : Unit is radian. Horizontal surface is 0, Vertical surface is 1/2π / (double)
3	Incline to copy / (ImmutableIncline object)	-

The first argument of the second constructor is Orientation object which is defined in Incline class. It can express 16 orientations (N, NNW, NW, WNW, W, WSW, SW, SSW, S, SSE, SE, ESE, E, ENE, NE, NNE).
Vertical angle of incline is expressed by radian, where horizontal surface is 0 and vertical surface is 1/2π.
The third constructor is a copy constructor. With calling third constructor, Incline object is initialized with the given ImmutableIncline object.
Table 5.3 and table 5.4 shows the methods and properties defined in the Incline class.

Table 5.3 The properties defined in the Inline class
Name	Description	Has set accessor	Unit	Type
ConfigurationFactorToSky	Configuration factor to the sky	-	-	double
HorizontalAngle	Horizontal angle of the inclined plane	-	Radian / South is 0, west is negative, east is positive	double
VerticalAngle	Vertical angle of the inclined plane	-	Radian / Horizontal surface is 0, vertical surface is 1/2π	double

Table 5.4 The methods defined in the Incline class
Name	Description
GetDirectSolarRadiationRate	Description	Calculate cosine θ of incident angle to the normal direction of the inclined plane.
	Return	Cosine θ of incident angle to the normal direction of the inclined plane.
	Arg.1	Sun (ImmutableSun object)	-	-
GetTanPhiAndGamma	Description	Calculate profile angle φ and angle between solar azimuth and normal direction of the inclined plane.
	Return	-
	Arg.1	Sun (ImmutableSun object)	Arg.2	Output : Tangent of profile angle φ
	Arg.3	Output :Tangent of angle between solar altitude and normal direction of the inclined plane
Reverse	Description	Reverse the Incline object
	Return	-

To calculate a radiation from sun, 3D positional relation between sun and incline (Figure 5.1).

γ is an angle between solar azimuth and normal direction of the inclined plane. φ is an angle between solar altitude and normal direction of the inclined plane. φ is called profile angle. φ and γ can be obtained by GetTanPhiAndGamma method. The first argument is a Sun object, which will be described later in section 5.2.3. The 2nd and 3rd argument are the outputs, tangent φ and tangent γ.

θ is an angle between incident angle and the normal direction of the inclined plane. θ can be obtained by GetDirectSolarRadiationRate method. The first argument is a Sun object. The returned value is cosine θ. This value is used when calculate an insolation on the inclined plane from the direct normal radiation.

The inclined plane can be reversed with calling Reverse method.

Figure 5.1 3D positional relation between sun and incline

### Sky class

Various static methods related to sky state are defined in the Sky class. Table 5.5 shows the methods defined in the Sky class.

Table 5.5 The methods defined in the Sky class
Name	Description
DegreeToRadian	Description	Convert an unit of angle from degree to radian
	Return	Angle [radian]
	Arg.1	Angle [degree]	-	-
GetAtmosphericRadiation	Description	Calculate atmospheric radiation [W/m2]
	Return	Atmospheric radiation [W/m2]
	Arg.1	Dry-bulb temperature of outdoor moist air[C]	Arg.2	Cloud cover ratio [-] (0~1)
	Arg.3	Water vapor pressure [kPa]
GetNocturnalRadiation	Description	Calculate nocturnal radiation [W/m2]
	Return	Calculate nocturnal radiation [W/m2]
	Arg.1	Dry-bulb temperature of outdoor moist air[C]	Arg.2	Cloud cover ratio [-] (0~1)
	Arg.3	Water vapor pressure [kPa]
RadianToDegree	Description	Convert an unit of angle from radian to degree.
	Return	Angle [degree]
	Arg.1	Angle [radian]	-	-

### Sun class
#### Constructor

The Sun class expresses sun. Information about longitude and latitude at the location must be given as argument in the constructor of the Sun to calculate azimuth and altitude of sun. Table 5.6 shows the constructors of the Sun class.

Table 5.6 The arguments of the Sun class
No.	Arg.1	Arg.2	Arg.3
1	Latitude [degree] (double)	Longitude [degree] (double)	Longitude of the standard time meridian [degree]
2	City to calculate sun position / (City object)	-	-
3	Copy constructor / (ImmutableSun)	-	-

An argument of the second constructor is City enumerator defined in the Sun class. More than 100 cities in the world are defined. A Sun object is initialized with longitude and latitude where the city is located. Below is a sample constructor call.

Sun sun = new Sun(Sun.City.Tokyo);
#### static method

Some basic methods related to sun position or solar radiation are defined in Sun class. Table 5.7 and Table 5.8 shows the static methods defined in the Sun class.

Table 5.7 The static methods related to sun position
Name	Description
GetEquationOfTime	Description	Caluculate an equation of the time.
	Return	Equation of the time.
	Arg.1	Date and time (DateTime object)
GetHourAngle	Description	Calculate hour angle from the location and the equation of the time.
	Return	Hour angle [°]
	Arg.1	Equation of the time.	Arg.2	Longitude [degree]
	Arg.3	Longitude of the standard time meridian [degree]	Arg.4	Date and time (DateTime object)
GetSunAltitude	Description	Calculate an altitude of sun. [radian]
	Return	Altitude of sun. [radian]
	Arg.1	Latitude [degree]	Arg.2	Longitude [degree]
	Args3	Longitude of the standard time meridian [degree]	Arg.4	Date and time (DateTime object)
GetSunAzimuth	Description	Caluculate an azimth of sun [radian]
	Return	Azimth of sun. [radian]
	Arg.1	Latitude [degree]	Arg.2	Longitude [degree]
	Arg.3	Longitude of the standard time meridian [degree]	Arg.4	Date and time (DateTime object)
GetSunDeclination	Description	Caluculate declination of sun. [degree]
	Return	Declination of sun. [degree]
	Arg.1	Date and time (DateTime object)	-	-
.GetSunPosition	Description	Calculate an altitude [radian] and a direction [radian] of sun
	Return	-
	Arg.1	Latitude [degree]	Arg.2	Longitude [degree]
	Arg.3	Longitude of the standard time meridian [degree]	Arg.4	Date and time (DateTime object)
	Arg.5	Output : Altitude of sun [radian]	Arg.6	Output : Direction of sun [radian]
GetSunRiseTime	Description	Calculate time of sun rise.
	Return	Time of sun rise (DateTime object)
	Arg.1	Latitude [degree]	Arg.2	Longitude [degree]
	Arg.3	Longitude of the standard time meridian [degree]	Arg.4	Date and time (DateTime object)
GetSunSetTime	Description	Calculate time of sun set.
	Return	Time of sun set (DateTime object)
	Arg.1	Latitude [degree]	Arg.2	Longitude [degree]
	Arg.3	Longitude of the standard time meridian [degree]	Arg.4	Date and time (DateTime object)

Table 5.8 The static methods related to solar radiation
Name	Description
GetExtraterrestrial / Radiation	Description	Calculate extraterrestrial radiation [W/m2]
	Return	Extraterrestrial radiation [W/m2]
	Arg.1	Days of the year (int object)	-	-
GetDirectNormalRadiation	Description	Calculate direct normal radiation from global horizontal radiation [W/m2] and diffuse horizontal radiation [W/m2]
	Return	Direct normal radiation [W/m2]
	Arg.1	Global horizontal radiation [W/m2]	Arg.2	Diffuse horizontal radiation [W/m2]
	Arg.3	Altitude of sun [radian]	-	-
GetDiffuseHorizontal / Radiation	Description	Calculate diffuse horizontal radiation [W/m2] from diract normal radiation [W/m2] and global horizontal radiation [W/m2].
	Return	Diffuse horizontal radiation [W/m2]
	Arg.1	Direct normal radiation [W/m2]	Arg.2	Diffuse horizontal radiation [W/m2]
	Arg.3	Altitude of sun [radian]	-	-
GetGlobalHorizontal / Radiation	Description	Calculate global horizontal radiation from diffuse horizontal radiation [W/m2] and direct normal radiation [W/m2]
	Return	Global horizontal radiation [W/m2]
	Arg.1	Diffuse horizontal radiation [W/m2]	Arg.2	Direct normal radiation [W/m2]
	Arg.3	Altitude of sun [radian]	-	-
EstimateDiffuseAnd / DirectNormalRadiation	Description	Estimate diffuse horizontal radiation and direct normal radiation from global horizontal radiation.
	Return	-
	Arg.1	Global horizontal radiation [W/m2]	Arg.2	Longitude [degree]
	Arg.3	Latitude [degree]	Arg.4	Longitude of the standard time meridian [degree]
	Arg.5	Date and time (DateTime object)	Arg.6	Estimating Method
	Arg.7	Output : / Direct normal radiation [W/m2]	Arg.8	Output : Diffuse horizontal radiation [W/m2]

The value of latitude and longitude are given by degree unit (not radian). East longitude is positive value and west longitude is negative. North latitude is positive value and south latitude is negative. For example, the arguments for Tokyo city (lies at 139.45° east in longitude and 35.4° north in latitude) are 139 + 45/60 = 139.75 and 35 + 4 / 60 = 35.07. The arguments for Rio de Janeiro (lies at 22.57° west in longitude and 43.12° south in latitude) are -22 - 57/60 = -22.95 and -43 - 12/60 = -43.2.

In most cases, a climate observatory measures only the global horizontal radiation, and the direct normal radiation and the diffuse horizontal radiation are not measured. Therefore, many people proposed methods to estimate the direct normal radiation and the diffuse horizontal radiation from the global horizontal radiation[6]) [7]) [8]) [9]). In the Sun class, EstimateDiffuseAndDirectNormalRadiation method is defined. User can select estimating method by setting DiffuseAndDirectNormalRadiationEstimatingMethod enumerator for the 6th argument. 6 methods, the method of Berlage[10]), Matsuo[11]), Nagata[12]), Liu & Jordan[13]), Udagawa & Kimura[14]), Watanabe[15]), Akasaka[16]) and Miki[17]), can be selected.
[6] Kimura, K., Stephenson, D.G. : Solar radiation on cloudy days, ASHRAE Transactions, Vol. 75, Part 1 (1969), pp.227~234
[7] Bugler, J.W. : The determination of hourly insolation on an inclined plane using a diffuse irradiance model based on hourly measured global horizontal insolation, Solar Energy, 19 (1977), pp.477~491
[8] Orgill, J.F., Hollands, K.G.T. : Correlation equation for hourly diffuse radiation on a horizontal surface, Solar Energy, 19-4 (1977), pp.357~359
[9] Spencer, J.W. : A comparison of methods for estimating hourly diffuse solar radiation from global solar radiation, Solar Energy, 29-1 (1982), pp.19~32
[10] Berlage,Von H.P.:Zur Theorie der Beleuchtung einer horizontalen Flache durch Tageslicht,Meteorologische Zeitschrift, May 1928,pp.174-180
[11] 松尾陽:日本建築学会論文報告集,快晴時の日射について 日射量に関する研究2,pp.21-24,1960
[12] 永田忠彦:晴天空による水平面散乱の日射の式の試案,日本建築学会学術講演梗概集,1978
[13] Liu,B.Y.H & Jordan,R.C:The interrelationship and characteristic distribution of direct, diffuse and total solar radiation, solar energy, Vol.4, No.3, 1960
[14] 宇田川光弘,木村建一:水平面全天日射量観測値よりの直達日射量の推定,日本建築学会論文報告集,No.267,pp.83-90,1978, 0530
[15] 渡辺俊行:水平面全天日射量の直散分離と傾斜面日射量の推定,日本建築学会論文報告集,No.330,pp.96-108,19830830
[16] H.Akasaka:Model of circumsolar radiation and diffuse sky radiation including cloudy sky, ISES, Solar World Congress, 1991
[17] 三木信博:標準気象データの日射直散分離に関する研究 その6 日射直散分離法の提案,日本建築学会学術講演梗概集,pp.857-858,1991

#### Other properties and methods defined in Sun class

Table 5.9 shows the properties defined in the Sun class. Value of the properties except radiations (DiffuseHorizontalRadiation, DirectNormalRadiation and GlobalHorizontalRadiation) can be determined when the location and the date and time information is given. The location is given as an argument of the constructor. The date and time information can be given by Update method. The DateTime object is given as an argument.

sun.Update(dateTime);

Table 5.9 The properties defined in Sun class
Name	Description	Has set accessor	Unit	Type
Altitude	Altitude of sun	TRUE	radian	double
CurrentDateTime	Current date and time	-	-	DateTime
DiffuseHorizontalRadiation	Diffuse horizontal radiation	TRUE	W/m2	double
DirectNormalRadiation	Direct normal radiation	TRUE	W/m2	double
GlobalHorizontalRadiation	Global horizontal radiation	TRUE	W/m2	double
Latitude	Latitude of sun	-	degree	double
Longitude	Longitude of sun	-	degree	double
Orientation	Orientation of sun	-	radian	double
Revision	Revision of Sun instance. Revision number is updated whenever Update method is called.	-	-	uint
StandardLongitude	Longitude of the standard time meridian	-	degree	double
SunRiseTime	Time of sun rise	-	-	DateTime
SunSetTime	Time of sun set	-	-	DateTime

Three values of radiation, the global horizontal radiation, the diffuse horizontal radiation and the direct normal radiation are related to each other. The value of one can be estimated when the rest of two value are given (Figure 5.2). Table 5.10 shows static methods to calculate these radiations.

Table 5.10 The methods to calculate a value of radiations
Name	Arg.1	Arg.2
SetDirectNormalRadiation	Global horizontal radiation	Diffuse horizontal radiation
SetDiffuseHorizontalRadiation	Direct normal radiation	Global horizontal radiation
SetGlobalHorizontalRadiation	Diffuse horizontal radiation	Direct normal radiation

Figure 5.2 Relations among three radiations

## Sample programs of calculating weather state

Figure 5.3 shows a sample program which calculate radiation of sun. It estimates the diffuse horizontal radiation and the direct normal radiation from the global horizontal radiation. The insolations on the inclined planes are also calculated. Figure 5.4 shows the result of the program.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32	/// <summary>Sample program calculating weather state</summary> / private static void weatherTest() / { / //Create an instance of the Sun class. (Location is Tokyo) / Sun sun = new Sun(Sun.City.Tokyo); / //Set date and time information(1983/12/21 12:00) / DateTime dTime = new DateTime(1983, 12, 21, 12, 0, 0); / sun.Update(dTime); / //Create instances of the Incline class. Vertical south east surface and 45 degree west surface. / Incline seInc = new Incline(Incline.Orientation.SE, 0.5 * Math.PI); / Incline wInc = new Incline(Incline.Orientation.W, 0.25 * Math.PI); / //Estimate direct normal and diffuse horizontal radiation from global horizontal radiation (467 W/m2) / sun.EstimateDiffuseAndDirectNormalRadiation(467); / //Calculate insolation rate on the inclined plane. / double cosThetaSE, cosThetaW; / cosThetaSE = seInc.GetDirectSolarRadiationRate(sun); / cosThetaW = wInc.GetDirectSolarRadiationRate(sun); / Console.WriteLine("Location:Tokyo, Date and time:12/21 12:00"); / Console.WriteLine("Altitude of sun=" + Sky.RadianToDegree(sun.Altitude).ToString("F1") + " degree"); / Console.WriteLine("Orientation of sun=" + Sky.RadianToDegree(sun.Orientation).ToString("F1") + " degree"); / Console.WriteLine("Direct normal radiation=" + sun.DirectNormalRadiation.ToString("F1") + " W/m2"); / Console.WriteLine("Diffuse horizontal radiation=" + sun.GlobalHorizontalRadiation.ToString("F1") + " W/m2"); / Console.WriteLine("Direct normal radiation to SE surface=" + (sun.DirectNormalRadiation * cosThetaSE).ToString("F1") + " W/m2"); / Console.WriteLine("Direct normal radiation to W surface=" + (sun.DirectNormalRadiation * cosThetaW).ToString("F1") + " W/m2"); / Console.Read(); / }

Figure 5.3 The sample program which calculate radiation of sun

Location:Tokyo, Date and time:12/21 12:00 / Altitude of sun=30.7 degree / Orientation of sun=5.4 degree / Direct normal radiation=650.2 W/m2 / Diffuse horizontal radiation=467.0 W/m2 / Direct normal radiation to SE surface=356.1 W/m2 / Direct normal radiation to W surface=272.1 W/m2

Figure 5.4 The result of the program

# Calculating Thermal Load of Building

## Name space for calculating thermal load of building

Classes which calculate building thermal load belong to the “Popolo.ThermalLoad” name space. Table 6.1 shows principal members defined in the “Popolo.ThermalLoad” name space. Some classes described at the previous chapters are also used to calculate thermal load (Sun class, Incline class, MoistAir class and so on). Figure 6.1 shows a UML diagram which shows the relations among classes used to calculate building thermal load. Most of the classes belongs to the “Popolo.ThermalLoad” name space.

Table 6.1 The principal members defined in Popolo.ThemalLoad name space
Name	Description
GlassPanes	The GlassPanes class is a model of one or more glass layers.
IHeatGain	The interface which shows a heat gain in the room.
MultiRoom	The MultiRoom class is a model of a multi-room. A multi-room consists of more than two rooms that are sepalated by a wall.
Outdoor	The Outdoor class is a model of an outdoor (It includes an information about sun position, moist air state, etc.).
Room	The Room class is a model of a single room. A room consists of more than two zones, that are not sepalated by a wall (ex. Interior zone and perimetor zone).
SunShade	The SunShade class is a model of a sun shade. Only simple shaped sun shade (Horizontal, vertical or gird) could be modeled with this class.
Wall	The Wall class is a model of a multi layered wall.
WallLayers	The WallLayers class is a model of a composition of the multi layered wall.
WallMaterial	The WallMaterial class is a model of a material used for wall.
WallSurface	The WallSurface class is a model of a wall surface. It contains information about emissivity and inclined degree of wall surface.
Window	The Window class is a model of a window.
WindowSurface	The WindowSurface class is a model of window surface. It contains information about emissivity and inclined degree of window surface.
Zone	The Zone class is a model of a single zone. A zone consists of wall surfaces and window surfaces.

Figure 6.1 The UML diagram of classes relating to Popolo.ThermalLoad name space

## General descriptions of classes defined in Popolo.ThermalLoad name space
### GlassPanes class

GlassPanes class expresses one or more glass layers. It calculates a characteristics of a window.
Two kinds of the constructor is defined in GlassPanes class. Table 6.2 shows the constructors of the GlassPanes class. The first constructor is the simplified one, which directly set the information about window characteristics (Overall transmissivity, overall absorptivity and heat transfer coefficient). The resistances at surfaces are not involved in heat transfer coefficient (arg. 3).
The second constructor is the detailed option, which calculates inter-reflection of glass panes. In this case, the lists of the GlassPanes.Pane class is given as an argument.

Table 6.2 The constructors of the GlassPanes class
No.	Argument 1	Argument 2	Argument 3
1	Overall transmissivity [-] / (double type)	Overall absorptivity [-] / (double type)	Heat transfer coefficient / [W/(m2 K)] (double type)
2	Lists of the glass panes / (Array of the GlassPanes.Pane objects)	-	-

There are three types of heat gains through the window of a building. The first is the transmission heat gain, the second is the absorption heat gain, and the last is the transfer heat gain (Figure 6.2). The solar incident falling on the window is partly reflected, partly absorbed and partly transmitted by the window glass. The absorbed heat partly go back to outdoor, and the rest infiltrate into the building. We call this infiltration rate to the solar incident as “overall absorptivity”.

Figure 6.2 Heat gains through a window

If a window consists of a single glass pane, overall transmissivity and overall absorptivity is equal to the transmissivity and the absorptivity of the single glass pane. If a window consists of more than one glass pane, detailed calculation is needed, since there occurs inter reflections among the glass panes. To calculate this phenomenon, use the second constructor of the GlassPanes class. The GlassPanes.Pane class is a model of a single glass pane which is the inner class of the GlassPanes class. Table 6.3 shows constructors of the GlassPanes.Pane class.

表6.3　GlassPanes.Paneコンストラクタの引数一覧
No.	Argument 1	Argument 2	Argument 3	Argument 4	Argument 5
1	Transmissivity [-] / (double type)	Absorptivity [-] / (double type)	Heat transfer coefficient [W/m2] (double type)	-	-
2	Transmissivity of outer side [-] / (double type)	Absorptivity of outer side [-] (double type)	Transmissivity of inner side [-] (double type)	Absorptivity of inner side [-] (double type)	Heat transfer coefficient [W/m2] (double type)
3	Predefined glass type. / (PredifinedGlassPane type)	-	-	-	-

In some glass panes, transmissivity and absorptivity of a surface is different from that of the opposite side surface. In this case, the second constructor should be used.
Some commonly-used glass panes are already defined in GlassPanes.Pane class. To make these glass panes, use the third constructor. The PredifinedGlassPane enumerator type is given as an argument.
By giving a GlassPanes.Pane array (The number of elements is M) to GlassPanes constructor, Overall transmissivity and overall reflectivity of the M layered glass panes are calculated according to equation 6.1 to 6.5. Where τT(M) is overall transmissivity, ρT(M) is overall reflectivity and αT(M)n is absorptivity of nth layer. The first element of array is the inside glass pane and the last element of array is the outside glass pane.

%tau_{T(m)}=%tau_{T(m-1)} X_r	(6.1)

%rho_{T(m)}=%rho_{Lm} + %tau_Rm %rho_{T(m-1)} X_r	(6.2)

%alpha_{T(m)n} = %alpha_{T(m-1)n} X_r	(6.3)

%alpha_{T(m)n} = %alpha_{Lm} + %alpha_Lm + %alpha_Rm %rho_{T(m-1)} X_r	(6.4)

X_r=%tau_Lm over {1 - %rho_Rm %rho_{T(m-1)}} , %tau_{T(1)}=%tau_{L 1} , %rho_{T(1)}=%rho_{L 1} , %alpha_{T(1)1}=1 - %tau_{L 1} - %rho_{L 1}	(6.5)

   τT : transmissivity [-], ρT : reflectivity [-], αT(m)n : absorptivity
   M : number of layers, L : outer side of glass pane, R : inner side of glass pane

The overall heat transmission coefficient and overall absorptivity of the glass panes can be calculated by equation 6.6 to 6.8.

K_GS = 1 / left ( 1 over %alpha_i + sum from m=0 to {M-1} R_{a(m)} + sum from m=0 to M R_{g(m)} + 1 over %alpha_o right )	(6.6)

B=sum from m=1 to M f_m %alpha_{T(m)}	(6.7)

f_m = 1 - K_GS left ( 1 over %alpha_i + sum from n=0 to {m-1} R_{a(n)} + sum from n=0 to {m-1} R_{g(n)} + 1 over %alpha_o right )	(6.8)

   KGS : overall heat transmission coefficients of the glass panes [W/(m2 K)], Ra : resistance of the air gap [(m2 K)/W]
   Rh : resistance of the glass pane [(m2 K)/W], fm : infiltration rate of absorbed heat gain at mth layer into a room
   αo : overall heat transfer coefficient at outside glass surface [W/(m2 K)], αi : overall heat transfer coefficient at inside glass surface [W/(m2 K)]
   B : overall heat absorptivity of glass panes [-]

Table 6.4 shows properties of GlassPanes class.

Table 6.4 The properties of the GlassPanes class
Name	Description	Has set accessor	Unit	Type
AngularDependenceCoefficients	Angular dependence of the solar heat gain coefficient	TRUE	-	double[]
ConvectiveRate	Convective rate of heat gain	TRUE	-	double
HeatTransferCoefficientOfGlass	Heat transfer coefficient of glass (The resistances at surfaces are not involved).	-	W/(m2K)	double
LongWaveEmissivity	Long wave emissivity of outer surface	TRUE	-	double
OverallAbsorptivity	Overall absorptance	-	-	double
OverallHeatTransmissionCoefficient	Overall heat transmission coefficient	-	W/(m2K)	double
OverallTransmissivity	Overall transmissivity	-	-	double
RadiativeRate	Rdiative rate of heat gain	TRUE	-	double

AngularDependenceCoefficients is coefficients to calculate angular dependence of the solar heat gain. The angular dependence can be calculated by equation 6.9. Default value of coefficients are Ai = {3.4167, -4.389, 2.4948, -0.5224}. Figure 6.3 shows angular dependence with default value. These coefficients give reasonable result in the most cases.

%tau_D over %tau_N = sum from i=1 to N A_i cos^i %theta	(6.9)

   τN : transmissivity when the solar incident angle is 90 degree [-], τD : transmissivity when the solar incident angle is θ degree [-]
   Ai : coefficients to calculate angular dependence of the solar heat gain [-]

Figure 6.3 Angular dependence

ConvectiveRate and RadiativeRate properties shows the convective and the radiative rate of a heat gain. These properties takes value between 0 to 1.
LongWaveEmissivity is used to calculate a heat loss by a nocturnal radiation.
Overall heat transfer coefficients at surfaces are not involved in HeatTransferCoefficientOfGlass.

Table 6.5 shows methods defined in GlassPanes class.

Table 6.5 The methods defined in the GlassPanes class
Name	Description
Copy	Description	Copy other GlassPanes object
	Return	-
	Arg.1	Target GlassPanes object to copy / (ImmutableGlassPanes type)	-	-
GetIncidentAngleCharacteristic	Description	Calculate incident angle characteristic
	Return	Incident angle characteristic of the glass panes.
	Arg.1	Cosine of incident angle (cosθ)	-	-
SetHeatTransfer / CoefficientsOfAirGaps	Description	Set heat transfer coefficients [W/(m2-K)] of air gaps
	Return	-
	Arg.1	Index of air gap :0 is room side	Arg.2	heat transfer coefficients [W/(m2-K)] of air gap
SetInsideOverallHeat / TransferCoefficient	Description	Set inside overall heat transfer coefficient [W/(m2-K)].
	Return	-
	Arg.1	inside overall heat transfer coefficient [W/(m2-K)]	-	-
SetOutsideOverallHeat / TransferCoefficient	Description	Set outside overall heat transfer coefficient [W/(m2-K)].
	Return	-
	Arg.1	outside overall heat transfer coefficient [W/(m2-K)]	-	-

If glass panes consist of more than one pane, heat transfer coefficients of air gaps must be given by SetHeatTransferCoefficientsOfAirGaps method.

Figure 6.4 shows a sample program which calculates the characteristics of a glass panes. Triple layered glass panes are created and some characteristics are written to the standard output stream. .
Three transparent glasses are created in the line 4 to 10. A instance of the GlassPanes class is created in the line 13 with these transparent glasses. The heat transfer coefficients of air gap and the overall heat transfer coefficients at the glass surface are initialized in the line 16 to 21. In the line 24 to 28, the characteristics of the glass panes are written to the standard output stream.
The outside glass pane is replaced by heat reflecting glass in the line 32 for comparison of characteristics.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40 / 41 / 42 / 43 / 44 / 45 / 46 / 47 / 48 / 49 / 50 / 51 / 52 / 53 / 54 / 55 / 56	/// <summary>Sample program calculating the charateristics of a glass panes</summary> / private static void glassPanesTest() / { / //Create an array of the GlassPanes.Glass class / GlassPanes.Pane[] panes = new GlassPanes.Pane[3]; / //Create a transparent glass (3mm). / panes[0] = new GlassPanes.Pane(0.79, 0.07, 0.85, 0.07, 131); //Inside of the window / panes[1] = new GlassPanes.Pane(0.79, 0.07, 0.85, 0.07, 131); / panes[2] = new GlassPanes.Pane(0.79, 0.07, 0.85, 0.07, 131); //Outside of the window / //Create an instance of GlassPanes class / GlassPanes glass = new GlassPanes(panes); / //Set heat transfer coefficients[W/(m2-K)] of air gap / glass.SetHeatTransferCoefficientsOfGaps(0, 1 / 0.12); / glass.SetHeatTransferCoefficientsOfGaps(1, 1 / 0.12); / //Set overall heat transfer coefficients[W/(m2-K)] at the surface of glass. / glass.SetInsideOverallHeatTransferCoefficient(9.26); //Inside of the window / glass.SetOutsideOverallHeatTransferCoefficient(23.26); //Outside of the window / //Check the characteristics of the glass panes. / Console.WriteLine("Transparent glass(3mm) * 3"); / Console.WriteLine("Overall transmissivity[-] = " + glass.OverallTransmissivity.ToString("F2")); / Console.WriteLine("Overall absorptivity[-] = " + glass.OverallAbsorptivity.ToString("F2")); / Console.WriteLine("Heat transfer coefficient of glass[-] = " + glass.HeatTransferCoefficientOfGlass.ToString("F2")); / Console.WriteLine("Heat transmission coefficient of glass[-] = " + glass.HeatTransmissionCoefficient.ToString("F2")); / Console.WriteLine(); / //Change the outside glass pane to heat reflecting glass(6mm) / panes[0] = new GlassPanes.Pane(GlassPanes.Pane.PredifinedGlassPane.HeatReflectingGlass06mm); / //Check the characteristics of a single glass pane. / Console.WriteLine("Heat reflecting glass(6mm)"); / Console.WriteLine("Transmissivity[-] = " + panes[0].OuterSideTransmissivity.ToString("F2")); / Console.WriteLine("absorptivity[-] = " + panes[0].OuterSideAbsorptivity.ToString("F2")); / Console.WriteLine("Reflectivity[-] = " + panes[0].OuterSideReflectivity.ToString("F2")); / Console.WriteLine(); / //Create an instance of GlassPanes class. Other properties are same as above / glass = new GlassPanes(panes); / glass.SetHeatTransferCoefficientsOfGaps(0, 1 / 0.12); / glass.SetHeatTransferCoefficientsOfGaps(1, 1 / 0.12); / glass.SetInsideOverallHeatTransferCoefficient(9.26); //Inside of the window / glass.SetOutsideOverallHeatTransferCoefficient(23.26); //Outside of the window / //Check the characteristics of the glass panes. / Console.WriteLine("Heat reflecting glass(6mm) + Transparent glass(3mm) * 2"); / Console.WriteLine("Overall transmissivity[-] = " + glass.OverallTransmissivity.ToString("F2")); / Console.WriteLine("Overall absorptivity[-] = " + glass.OverallAbsorptivity.ToString("F2")); / Console.WriteLine("Heat transfer coefficient of glass[-] = " + glass.HeatTransferCoefficientOfGlass.ToString("F2")); / Console.WriteLine("Heat transmission coefficient of glass[-] = " + glass.HeatTransmissionCoefficient.ToString("F2")); / Console.Read(); / }

Figure 6.4 The sample program which calculates the characteristics of a glass panes

Figure 6.5 shows the result of the simulation. The transmissivity of the second glass panes is smaller than that of the first glass panes, since the reflectivity of the heat reflecting glass is bigger than the normal transparent glass.

Transparent glass(3mm) * 3 / Overall transmissivity[-] = 0.50 / Overall absorptivity[-] = 0.13 / Heat transfer coefficient of glass[-] = 3.80 / Heat transmission coefficient of glass[-] = 2.42 / Heat reflecting glass(6mm) / Transmissivity[-] = 0.60 / absorptivity[-] = 0.10 / Reflectivity[-] = 0.30 / Heat reflecting glass(6mm) + Transparent glass(3mm) * 2 / Overall transmissivity[-] = 0.39 / Overall absorptivity[-] = 0.11 / Heat transfer coefficient of glass[-] = 3.70 / Heat transmission coefficient of glass[-] = 2.37

Figure 6.5 The result of the simulation

### Window class

The Window class is a model of a window. It is initialized by GlassPanes object described in the section 6.2.1. Table 6.6 shows the constructors of the Window class.

Table6.6 The constructors of the Window class
No.	Argument 1	Argument 2	Argument 3
1	Multi-layered glass panes / (ImmutableGlassPanes object)	-	-
2	Multi-layered glass panes / (ImmutableGlassPanes object )	Inclined plane of outside surface / (ImmutableIncline object)	-
3	Multi-layered glass panes / (ImmutableGlassPanes object)	Inclined plane of outside surface / (ImmutableIncline object)	Sun shade for the window / (ImmutableSunShade object)

The second argument of the constructor is a Incline object described in the section 5.2.1. The third argument is a SunShade object which calculates a shading rate of the window. The SunShade class will be described later in the section 6.2.4.

Table 6.7 shows the properties defined in the Window class.

Table 6.7 The properties defined in the Window class.
Name	Description	Has set accessor	Unit	Type
AbsorbedHeatGain	Heat gain by absorption	-	W	double
Albedo	Albedo	TRUE	-	double
ConvectiveHeatGain	Radiative heat gain	-	W	double
Glass	Multi-layered glass	-	-	ImmutableGlassPanes
IndoorDrybulbTemperature	Indoor drybulb temperature	TRUE	°C	double
IndoorSurfaceTemperature	Indoor surface temperature	-	°C	double
NocturnalRadiation	Nocturnal radiation	TRUE	W/m2	double
OutdoorDrybulbTemperature	Outdoor drybulg temperature	TRUE	°C	double
OutdoorSideIncline	Incline of outside surface	-	-	ImmutableIncline
OutdoorSurfaceTemperature	Outdoor surface temperature	-	°C	double
RadiativeHeatGain	Radiative heat gain	-	W	double
Shade	Sun shade of the window	TRUE	-	ImmutableSunShade
ShadowRate	Shadow rate	TRUE	-	double
Sun	Sun	TRUE	-	ImmutableSun
SurfaceArea	Surface are of the window	TRUE	m2	double
TransferHeatGain	Heat gain by heat transfer	-	W	double
TransmissionHeatGain	Heat gain by transmission	-	W	double

Some boundary conditions (Albedo, OutdoorDrybulbTemperature, IndoorDrybulbTemperature and NocturnalRadiation properties ) must be given to calculate a heat transfer through the window. An information about sun shade of the window is given as Shade property to calculate shadow rate, otherwise user should specify shadow rate directly by ShadowRate property. The information about solar radiations (direct normal radiation, diffuse horizontal radiation and global horizontal radiation) are given by Sun property. It is Sun object described at section 5.2.3.
When the boundary conditions are fixed, heat transfer (absorbed, transfer and transmission heat gain) through the window is determined. These heat gains are separated into two kinds of heat gains, convective heat gain and radiative heat gain. The convective heat gain is the heat gain that directly raise the temperature of a room. The radiative heat gain is the heat gain that first raise the temperature of room wall surfaces or other window surfaces. Therefore, the radiative heat gain has a time delay to the room temperature. Sum of the AbsorbedHeatGain, TransferHeatGain and TransmissionHeatGain is equal to ConvectiveHeatGain and RadiativeHeatGain.

Figure 6.6 shows a sample program which calculates the heat gain from a window.

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40 / 41 / 42 / 43 / 44 / 45 / 46 / 47 / 48 / 49 / 50 / 51 / 52 / 53 / 54 / 55 / 56 / 57 / 58 / 59 / 60 / 61 / 62 / 63 / 64 / 65	/// <summary>Sample program calculating the heat gain from the window</summary> / private static void windowTest() / { / //A sample weather data / //direct normal radiation [W/m2] / double[] wdIdn = new double[] { 0, 0, 0, 0, 0, 244, 517, 679, 774, 829, 856, 862, 847, 809, 739, 619, 415, 97, 0, 0, 0, 0, 0, 0 }; / //diffuse horizontal radiation [W/m2] / double[] wdIsky = new double[] { 0, 0, 0, 0, 21, 85, 109, 116, 116, 113, 110, 109, 111, 114, 116, 114, 102, 63, 0, 0, 0, 0, 0, 0 }; / //drybulb temperature [C] / double[] wdDbt = new double[] { 27, 27, 27, 27, 27, 28, 29, 30, 31, 32, 32, 33, 33, 33, 34, 33, 32, 32, 31, 30, 29, 29, 28, 28 }; / //nocturnal radiation [W/m2] / double[] wdRN = new double[] { 24, 24, 24, 24, 24, 24, 25, 25, 25, 25, 26, 26, 26, 26, 26, 26, 26, 25, 25, 25, 25, 24, 24, 24 }; / //Create a window with a single 3mm transparent glass pane / GlassPanes.Pane pane = new GlassPanes.Pane(GlassPanes.Pane.PredifinedGlassPane.TransparentGlass03mm); / GlassPanes glassPane = new GlassPanes(pane); / Window window = new Window(glassPane); / //Set wall surface information / WindowSurface outsideWindowSurface = window.GetSurface(true); / outsideWindowSurface.OverallHeatTransferCoefficient = 23d; / outsideWindowSurface.Albedo = 0.2; / WindowSurface insideWindowSurface = window.GetSurface(false); / insideWindowSurface.OverallHeatTransferCoefficient = 9.3; / //Set incline of an outdoor surface : South, vertical incline / window.OutSideIncline = new Incline(Incline.Orientation.S, 0.5 * Math.PI); / //There is no sun shade / window.Shade = SunShade.EmptySunShade; / //Initialize sun. Tokyo : 7/21 0:00 / Sun sun = new Sun(Sun.City.Tokyo); / DateTime dTime = new DateTime(2001, 7, 21, 0, 0, 0); / sun.Update(dTime); / window.Sun = sun; / //Indoor drybulb temperature is constant (25C) / window.IndoorDrybulbTemperature = 25; / //Result : Title line / Console.WriteLine(" Time |Transmission[W]|Absorption[W]|Transfer[W]|Convective[W]|Radiative[W]"); / //execute simulation / for (int i = 0; i < 24; i++) / { / //Set radiations (calculate global horizontal radiation from direct normal and diffuse horizontal radiation) / sun.SetGlobalHorizontalRadiation(wdIsky[i], wdIdn[i]); / //Set nocturnal radiation / window.NocturnalRadiation = wdRN[i]; / //Set outdoor temperature / window.OutdoorDrybulbTemperature = wdDbt[i]; / //Output result / Console.WriteLine(dTime.ToShortTimeString().PadLeft(5) + " | " + window.TransmissionHeatGain.ToString("F1").PadLeft(13) + " | " + / window.AbsorbedHeatGain.ToString("F1").PadLeft(11) + " | " + window.TransferHeatGain.ToString("F1").PadLeft(9) + " | " + / window.ConvectiveHeatGain.ToString("F1").PadLeft(11) + " | " + window.RadiativeHeatGain.ToString("F1").PadLeft(11)); / //Update time / dTime = dTime.AddHours(1); / sun.Update(dTime); / } / Console.Read(); / }

Figure 6.6 The sample program which calculates the heat gain from the window

The arrays declared in the line 4~12 is a sample weather data. These are the value of direct normal radiation, diffuse horizontal radiation, drybulb temperature and nocturnal radiation of one day.
An instance of the GlassPanes class is created in the line 15 and 16. The transparent 3mm glass pane is created. A Window object is initialized with this GlassPanes object in the line 17.
A WindowSurface object is used to set surface state in the line 20~24. Overall heat transfer coefficients and albedo are set to WindowSurface object. Albedo is solar radiation reflectivity of ground surface. In urban areas, value of albedo is around 0.2.
Outdoor surface incline is set in the line 27. It is the south vertical window.
The sun shade is set in the line 30. In this sample, the window has no sun shade. The SunShade class will be described late in the section 6.2.4.
A instance of Sun class is created in the line 33~36. The location is Tokyo and the date is 7/21. It is 0:00 at the beginning of the simulation. The line from 45 to 62 is the iteration. It iterates 24 times to simulate 24 hours.
The three boundary conditions, solar radiation, nocturnal radiation and drybulb temperature is set in the line 47~52. The heat gains from the window is calculated since boundary conditions are fixed. All the heat gains are written to the standard output stream in the line 55~57. Finally, in the line 60 and 61, 1 hour is added to update the position of the sun.
Figure 6.7 shows the result of the simulation.

Time | Transmission[W] | Absorption[W] | Transfer[W] | Convective[W] | Radiative[W] / 0:00 | 0.0 | 0.0 | 12.9 | 5.8 | 7.1 / 1:00 | 0.0 | 0.0 | 12.9 | 5.8 | 7.1 / 2:00 | 0.0 | 0.0 | 12.9 | 5.8 | 7.1 / 3:00 | 0.0 | 0.0 | 12.9 | 5.8 | 7.1 / 4:00 | 9.7 | 0.3 | 13.2 | 6.0 | 7.4 / 5:00 | 40.3 | 1.1 | 20.4 | 9.7 | 11.8 / 6:00 | 60.4 | 1.6 | 27.4 | 13.0 | 15.9 / 7:00 | 77.0 | 2.0 | 34.3 | 16.3 | 20.0 / 8:00 | 91.7 | 2.4 | 41.2 | 19.6 | 24.0 / 9:00 | 134.4 | 3.5 | 48.7 | 23.5 | 28.7 / 10:00 | 190.5 | 5.0 | 50.2 | 24.8 | 30.4 / 11:00 | 229.5 | 6.0 | 57.7 | 28.7 | 35.0 / 12:00 | 236.3 | 6.2 | 57.9 | 28.8 | 35.2 / 13:00 | 208.2 | 5.4 | 57.1 | 28.2 | 34.4 / 14:00 | 154.5 | 4.0 | 62.2 | 29.8 | 36.4 / 15:00 | 97.9 | 2.6 | 54.2 | 25.6 | 31.2 / 16:00 | 64.8 | 1.7 | 46.9 | 21.9 | 26.7 / 17:00 | 31.9 | 0.8 | 46.1 | 21.1 | 25.8 / 18:00 | 0.0 | 0.0 | 38.8 | 17.4 | 21.3 / 19:00 | 0.0 | 0.0 | 32.3 | 14.5 | 17.8 / 20:00 | 0.0 | 0.0 | 25.8 | 11.6 | 14.2 / 21:00 | 0.0 | 0.0 | 25.8 | 11.6 | 14.2 / 22:00 | 0.0 | 0.0 | 19.4 | 8.7 | 10.7 / 23:00 | 0.0 | 0.0 | 19.4 | 8.7 | 10.7

Figure 6.7 The result of the simulation

### AirFlowWindow class

************

### SunShade class

The SunShade class is a model of a sun shade. Figure 6.8 shows the shapes of the sun shade that can be treated by SunShade class. To create these shaped sun shades, some static methods are defined in the SunShade class. These static methods must be used to create an instance of the SunShade class, since SunShade class doesn't have constructor. There is special static member, EmptySunShade property, to express empty sun shade.
Table 6.8 shows the properties defined in the SunShade class. Most of the properties are read only property.
Incline is described in the section 5.2.1. SunShade class can calculate a shadow rate at inclined plane like roof skylight.
An opening area can be reversed with IsReverse property. If the IsReverse property is true, the opening area is treated as the sun shade and the sun shade is treated as opening area. For example, we can calculate shadow rate of a dry area by reversing the horizontal sun shade (Figure 6.9).

Figure 6.8 Three types of the sun shade

Figure 6.9 Reverse the sun shade

Table 6.8 The properties defined in the SunShade class
Name	Description	Has set accessor	Unit	Type
BottomMargin	Bottom margin	-	m	double
Incline	Incline	TRUE	-	ImmutableIncline
IsReverse	Whether sun shade is reversed or not	TRUE	-	bool
LeftMargin	Length of left margin	-	m	double
Name	Name of sun shade	TRUE	-	string
Pendent	Length of pendent	-	m	double
RightMargin	Length of right margin	-	m	double
SunShadeShape	Shape type	-	-	SunShade.Shape
TopMargin	Length of top margin	-	m	double
WindowHeight	Height of the window	-	m	double
WindowWidth	Width of the window	-	m	double

Table 6.9 The static methods defined in the SunShade class
Name	Description
MakeGridSunShade	Function	Create grid sun shade.
	Return	grid sun shade.
	Arg.1	Window width [m]	Arg.2	Window height [m]
	Arg.3	Length of pendent [m]	Arg.4	Length of left margin [m]
	Arg.5	Length of right margin [m]	Arg.6	Length of top margin [m]
	Arg.7	Length of bottom margin [m]	Arg.8	Incline
MakeHorizontalSunShade	Function	Create horizontal sun shade.
	Return	horizontal sun shade.
	Arg.1	Window width [m]	Arg.2	Window height [m]
	Arg.3	Length of pendent [m]	Arg.4	Length of left margin [m]
	Arg.5	Length of right margin [m]	Arg.6	Length of top margin [m]
	Arg.7	Incline	-	-
MakeHorizontalSunShade	Function	Create horizontal (infinite length) sun shade.
	Return	horizontal (infinite length) sun shade.
	Arg.1	Window width [m]	Arg.2	Window height [m]
	Arg.3	Length of pendent [m]	Arg.4	Length of top margin [m]
	Arg.5	Incline	-	-
MakeVerticalSunShade	Function	Create left or right side wall sun shade
	Return	left or right side wall sun shade
	Arg.1	Window width [m]	Arg.2	Window height [m]
	Arg.3	Length of pendent [m]	Arg.4	Length of side [m]
	Arg.5	Set true if left side wall	Arg.6	Length of top margin[m]
	Arg.7	Length of bottom margin [m]	Arg.8	Incline
MakeVerticalSunShade	Function	Create left or right side wall (infinite length) sun shade
	Return	eft or right side wall (infinite length) sun shade
	Arg.1	Window width [m]	Arg.2	Window height [m]
	Arg.3	Length of pendent [m]	Arg.4	Length of side margin [m]
	Arg.5	Set true if left side wall	Arg.6	Incline
MakeVerticalSunShade	Function	Create both side wall sun shade
	Return	both side wall sun shade
	Arg.1	Window width [m]	Arg.2	Window height [m]
	Arg.3	Length of pendent [m]	Arg.4	Length of side margin [m]
	Arg.5	Length of top margin [m]	Arg.6	Length of bottom margin [m]
	Arg.7	Incline	-	-
MakeVerticalSunShade	Function	Create both side wall (infinite length) sun shade
	Return	both side wall (infinite length) sun shade
	Arg.1	Window width [m]	Arg.2	Window height [m]
	Arg.3	Length of pendent [m]	Arg.4	Length of side margin [m]
	Arg.5	Incline	-	-

### WallLayers class

　WallLayersクラスは1以上の材料で構成される層状の壁体を表現するためのクラスです。WallLayersクラスのプロパティと主要なメソッドを表6.10と表6.11に示します。AddLayerやSetLayerメソッドを利用しながら層の構成を設定し、GetOverallHeatTransferCoefficientメソッドで全体の熱貫流率[W/(m2K)]を計算するという流れになります。なお、本クラスは読み取り専用のImmutableWallLayersインターフェースを継承しています。
　単一の壁層を表現するには、WallLayersクラスのインナークラスであるLayerクラスを利用します。Layerクラスのコンストラクタを表6.12に示します。壁の材料と厚み、また、壁体が非常に厚い場合などには壁の分割数を設定します。

Table 6.10 WallLayersクラスのプロパティ一覧
プロパティ名称	内容	setアクセッサ	単位	型
LayerNumber	壁層の数	-	-	uint
Name	名称	○	-	string

Table 6.11 WallLayersクラスの主要メソッド
名称	内容
GetOverallHeatTransfer / Coefficient	概要	壁表面の総合熱伝達率 [W/(m2K)]を指定して熱貫流率 [W/(m2K)]を計算する
	戻り値	熱貫流率[W/(m2K)]
	引数1	表面1の総合熱伝達率 [W/(m2K)]	引数2	表面2の総合熱伝達率 [W/(m2K)]-
GetOverallHeatTransfer / Coefficient	概要	熱貫流率[W/(m2K)]を計算する
	戻り値	-
	引数1	-	引数2	-
UsingMaterial	概要	壁素材を使っているか否かを返す
	戻り値	壁素材を使っているか否か
	引数1	壁素材 (ImmutableWallMaterial型)	-	-
AddLayer	概要	壁層を追加する
	戻り値	-
	引数1	壁層 (Layer型)	引数2	-
GetLayer	概要	壁層配列を取得する
	戻り値	壁層配列 (Layer型)
	引数1	-	引数2	-
GetLayer	概要	指定の位置の壁層を取得する
	戻り値	壁層 (Layer型)
	引数1	壁層番号	引数2	-
RemoveLayer	概要	壁層を削除する
	戻り値	-
	引数1	壁層番号	引数2	-
SetLayer	概要	指定の位置に壁層を設定する
	戻り値	-
	引数1	壁層番号	引数2	壁層 (Layer型)

表6.12　WallLayers.Layerコンストラクタの引数一覧
No.	引数1	引数2	引数3
1	壁材料 (ImmutableWallMaterial型)	壁の厚み (double型)	-
2	壁材料 (ImmutableWallMaterial型)	壁の厚み (double型)	壁の分割数 (uint型)

　壁材料を表現するためにはWallMaterialクラスを利用します。表6.13にWallMaterialコンストラクタの引数一覧を示します。素材の名称、熱伝導率[W/(m K)]、容積比熱[kJ/(m3 K)]が主な情報です。2番目のコンストラクタを利用することで、予め定義されているいくつかの主要な材料の物性で初期化することができます。表6.15に定義済の壁材料一覧を示します。3番目のコンストラクタはコピーコンストラクタです。表6.14にWallMaterialクラスのプロパティ一覧を示します。
　なお、空気層の場合にはVolumetricSpecificHeatプロパティを0とし、ThermalConductivityプロパティに熱コンダクタンス[W/(m2 K)]を設定します。

表6.13　WallMaterialコンストラクタの引数一覧
No.	引数1	引数2	引数3
1	素材名称 (string型)	熱伝導率 [W/(m K)] (double型)	容積比熱 [kJ/(m3 K)] (double型)
2	既定義の素材 / (WallMaterial.PredifinedMaterials列挙型)	-	-
3	壁材料 (ImmutableWallMaterial型)	-	-

表6.14　WallMaterialクラスのプロパティ一覧
プロパティ名称	内容	setアクセッサ	単位	型
Material	素材の種類	-	-	WallMaterial.PredifinedMaterials
Name	名称	○	-	string
ThermalConductivity	熱伝導率	○	W/(m K)	double
VolumetricSpecificHeat	容積比熱	○	kJ/(m3 K)	double

　以上に示したように、多層壁の材料の熱伝導率λと厚みlが与えられると、式6.10に従って、壁体全体の熱貫流率が計算できるようになります。ここで、α1, α2は壁表面の総合熱伝達率 [W/(m2 K)]、Cairは壁層に含まれる空気層の熱コンダクタンス [W/(m2 K)]です。

K=1 / left lbrace 1 over %alpha_1 + sum {l over %lambda} + sum {1 over C_air} + 1 over %alpha_2 right rbrace	(6.10)

　図6.9に、WallLayersクラスとWallMaterialクラスを利用して、多層壁の熱貫流率を計算するプログラムの例を示します。
　合板、非密閉の空気層、鉄筋コンクリート、漆喰の4層で構成される多層壁で、6~15行目ではそれぞれの壁材料を作成しています。合板、非密閉の空気層、鉄筋コンクリートに関しては定義済の材料を利用して初期化を行い、漆喰については熱伝導率と容積比熱を直接に指定して作成しています。
　17~25行では、これらの壁材料を使って、多層壁を作成しています。それぞれの厚みは20mm, 10mm, 150mm, 10mmです。
　27~35行で結果の書き出しを行っており、各層の材料の名称、厚みの他、全体の熱貫流率を算出しています。また、38行目では鉄筋コンクリートを軽量コンクリートに入れ替えており、40~47行で、その計算結果を書き出しています。図6.11に、計算結果を示します。

Table 6.15 Members of the PredifinedMaterials enumerator
列挙型名称	壁材料	熱伝 / 導率	容積 / 比熱	列挙型名称	壁材料	熱伝 / 導率	容積 / 比熱
Mortar	セメント・モルタル	1.512	1591	SprayedRockWool	吹付けロックウール	0.047	167.9
ReinforcedConcrete	コンクリート	1.6	1896	BeadMethodPolystyreneFoam_S	ビーズ法ポリスチレンフォーム特号	0.034	33.9
LightweightAggregateConcrete1	軽量骨材コンクリート1種	0.81	1900	BeadMethodPolystyreneFoam_1	ビーズ法ポリスチレンフォーム1号	0.036	37.7
LightweightAggregateConcrete2	軽量骨材コンクリート2種	0.58	1599	BeadMethodPolystyreneFoam_2	ビーズ法ポリスチレンフォーム2号	0.037	31.4
AutomaticLevelControl	軽量気泡コンクリートパネル / ALCパネル	0.17	661.4	BeadMethodPolystyreneFoam_3	ビーズ法ポリスチレンフォーム3号	0.04	25.1
Brick	普通れんが	0.62	1386	BeadMethodPolystyreneFoam_4	ビーズ法ポリスチレンフォーム4号	0.043	18.8
FireBrick	耐火れんが	0.99	1553	ExtrudedPolystyreneFoam_1	押出法ポリスチレンフォーム1種	0.04	25.1
Copper	銅	370.1	3144	ExtrudedPolystyreneFoam_2	押出法ポリスチレンフォーム2種	0.034	25.1
Aluminum	アルミニウム合金	200	2428	ExtrudedPolystyreneFoam_3	押出法ポリスチレンフォーム3種	0.028	25.1
Steel	鋼材	53.01	3759	RigidUrethaneFoam_1_1	硬質ウレタンフォーム保温版1種1号	0.024	56.1
Lead	鉛	35.01	1469	RigidUrethaneFoam_1_2	硬質ウレタンフォーム保温版1種2号	0.024	44
StainlessSteel	ステンレス鋼	15	3479	RigidUrethaneFoam_1_3	硬質ウレタンフォーム保温版1種3号	0.026	31.4
FloatGlass	フロートガラス	1	1914	RigidUrethaneFoam_2_1	硬質ウレタンフォーム保温版2種1号	0.023	56.1
PolyvinylChloride	PVC(塩化ビニル)	0.17	1023	RigidUrethaneFoam_2_2	硬質ウレタンフォーム保温版2種2号	0.023	44
Wood1	天然木材1類（桧、杉、えぞ松等）	0.12	519.1	RigidUrethaneFoam_2_3	硬質ウレタンフォーム保温版2種3号	0.024	31.4
Wood2	天然木材2類（松、ラワン等）	0.15	648.8	RigidUrethaneFoam_InSite	硬質ウレタンフォーム（現場発泡品）	0.026	49.8
Wood3	天然木材3類 / （ナラ、サクラ、ブナ等）	0.19	845.6	PolyethyleneFoam_A	ポリエチレンフォーム Ａ	0.038	62.8
Plywood	合板	0.19	716	PolyethyleneFoam_B	ポリエチレンフォーム Ｂ	0.042	62.8
WoodWoolCement	断熱木毛セメント板	0.1	841.4	PhenolicFoam_1_1	フェノールフォーム保温版 1種1号	0.033	37.7
WoodChipCement	木片セメント板	0.17	1679	PhenolicFoam_1_2	フェノールフォーム保温版 1種2号	0.03	37.7
HardBoard	ハードボード	0.17	1233	PhenolicFoam_2_1	フェノールフォーム保温版 2種1号	0.036	56.5
ParticleBoard	パーティクルボード	0.15	715.8	PhenolicFoam_2_2	フェノールフォーム保温版 2種2号	0.034	56.5
PlasterBoard	せっこうボード	0.17	1030	InsulationBoard_A	A級インシュレーションボード	0.049	324.8
GypsumPlaster	せっこうプラスター	0.6	1637	TatamiBoard	タタミボード	0.045	15.1
WhiteWash	漆喰	0.7	1093	SheathingInsulationBoard	シージングボード	0.052	390.1
SoilWall	土壁	0.69	1126	CelluloseFiberInsulation_1	吹込用セルローズファイバー断熱材1	0.04	37.7
FiberCoating	繊維質上塗材	0.12	4.2	CelluloseFiberInsulation_2	吹込用セルローズファイバー断熱材2	0.04	62.8
Tatami	畳床	0.11	527.4	Soil	土壌（ローム質）	1.047	3340
Tile	タイル	1.3	2018	ExpandedPolystyrene	EPS	0.035	300
PlasticTile	プラスチック（P）タイル	0.19	4.2	CoveringMaterial	外装材	0.14	1680
GlassWoolInsulation_10K	グラスウール断熱材 10K相当	0.05	8.4	Linoleum	合成樹脂・リノリウム	0.19	1470
GlassWoolInsulation_16K	グラスウール断熱材 16K相当	0.045	13.4	Carpet	カーペット	0.08	318
GlassWoolInsulation_24K	グラスウール断熱材 24K相当	0.038	20.1	AsbestosPlate	石綿スレート	1.2	1820
GlassWoolInsulation_34K	グラスウール断熱材 32K相当	0.036	26.8	SealedAirGap	密閉空気層	5.8	0
HighGradeGlassWoolInsulation_16K	高性能グラスウール断熱材 / 16K相当	0.038	13.4	AirGap	非密閉空気層	11.6	0
HighGradeGlassWoolInsulation_24K	高性能グラスウール断熱材 / 24K相当	0.036	20.1	PolystyreneFoam	ポリスチレンフォーム	0.035	80
BlowingGlassWoolInsulation_13K	吹込用グラスウール断熱材1種 / 13K相当	0.052	10.9	StyreneFoam	スチレン発泡板	0.035	10
BlowingGlassWoolInsulation_18K	吹込用グラスウール断熱材2種 / 18K相当	0.052	16.7	RubberTile	ゴムタイル	0.4	784
BlowingGlassWoolInsulation_30K	吹込用グラスウール断熱材2種 / 30K相当	0.04	29.3	Kawara	瓦	1	1506
BlowingGlassWoolInsulation_35K	吹込用グラスウール断熱材2種 / 35K相当	0.04	37.7	LightweightConcrete	軽量コンクリート	0.78	1607
RockWoolInsulationMat	住宅用ロックウール断熱材 マット	0.038	33.5	Asphalt	アスファルトルーフィング	0.11	920
RockWoolInsulationFelt	住宅用ロックウール断熱材 / フェルト	0.038	41.9	FrexibleBoard	フレキシブルボード	0.35	1600
RockWoolInsulationBoard	住宅用ロックウール断熱材 ボード	0.036	58.6	CalciumSilicateBoard	珪酸カルシウム板	0.13	680
BlowingRockWoolInsulation_25K	吹込用ロックウール断熱材 25K	0.047	20.9	PhenolicFoam	高性能フェノールボード	0.02	37.7
BlowingRockWoolInsulation_35K	吹込用ロックウール断熱材 35K	0.051	29.3	GNT	花崗岩	4.3	2.9
RockWoolAcousticBoard	ロックウール化粧吸音板	0.058	293.9	AcrylicResin	アクリル樹脂	0.21	1666

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40 / 41 / 42 / 43 / 44 / 45 / 46 / 47 / 48 / 49 / 50 / 51	private static void wallOverallHeatTransferCoefTest() / { / //多層壁オブジェクトを作成 / WallLayers wLayers = new WallLayers("熱貫流率計算用多層壁"); / //壁層の素材を作成 / WallMaterial[] materials = new WallMaterial[4]; / //第1層：合板 / materials[0] = new WallMaterial(WallMaterial.PredefinedMaterials.Plywood); / //第2層：非密閉空気層 / materials[1] = new WallMaterial(WallMaterial.PredefinedMaterials.AirGap); / //第3層：鉄筋コンクリート / materials[2] = new WallMaterial(WallMaterial.PredefinedMaterials.ReinforcedConcrete); / //第4層：漆喰 / materials[3] = new WallMaterial("漆喰", 0.7, 1000); / //壁の各層を作成 / //合板:20mm / wLayers.AddLayer(new WallLayers.Layer(materials[0], 0.02)); / //空気層:厚みは関係なし / wLayers.AddLayer(new WallLayers.Layer(materials[1], 0.01)); / //鉄筋コンクリート:150mm / wLayers.AddLayer(new WallLayers.Layer(materials[2], 0.15)); / //漆喰:10mm / wLayers.AddLayer(new WallLayers.Layer(materials[3], 0.01)); / //結果書き出し / Console.WriteLine("壁層の構成"); / for (uint i = 0; i < wLayers.LayerNumber; i++) / { / WallLayers.Layer layer = wLayers.GetLayer(i); / Console.WriteLine("第" + (i + 1) + "層：" + layer.Material.Name + "(" + layer.Thickness + "m)"); / } / Console.WriteLine("熱貫流率=" + wLayers.GetOverallHeatTransferCoefficient().ToString("F1") + " W/(m2-K)"); / Console.WriteLine(); / //軽量コンクリートに変えてみる / wLayers.SetLayer(2, new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.LightweightConcrete), 0.15)); / //結果書き出し / Console.WriteLine("壁層の構成"); / for (uint i = 0; i < wLayers.LayerNumber; i++) / { / WallLayers.Layer layer = wLayers.GetLayer(i); / Console.WriteLine("第" + (i + 1) + "層：" + layer.Material.Name + "(" + layer.Thickness + "m)"); / } / Console.WriteLine("熱貫流率=" + wLayers.GetOverallHeatTransferCoefficient().ToString("F1") + " W/(m2-K)"); / Console.Read(); / }

図6.10　多層壁の熱貫流率計算テスト

図6.11　実行結果
壁層の構成
第1層：合板(0.02m)
第2層：非密閉空気層(0.01m)
第3層：コンクリート(0.15m)
第4層：漆喰(0.01m)
熱貫流率=3.3 W/(m2-K)

壁層の構成
第1層：合板(0.02m)
第2層：非密閉空気層(0.01m)
第3層：軽量コンクリート(0.15m)
第4層：漆喰(0.01m)
熱貫流率=2.5 W/(m2-K)

### Wall class

　壁体の非定常熱伝導を計算するためには、Wallクラスを使用します。表6.16にWallクラスのコンストラクタを示します。6.2.5節で説明したWallLayerオブジェクトを与えることで壁層が初期化されます。
　表6.17にWallクラスの主要なプロパティを示します。この他、一般的な壁体の構築に関連する処理を表6.18に示します。

表6.16　Wallコンストラクタの引数一覧
No.	引数1	引数2
1	壁の構成 (ImmutableWallLayers型)	壁体名称 (string型)
2	壁の構成 (ImmutableWallLayers型)	-

表6.17　Wallクラスの主要なプロパティ一覧
プロパティ名称	内容	setアクセッサ	単位	型
TimeStep	計算時間間隔	○	sec	double
SurfaceArea	壁表面積	○	m2	double
Layers	壁層	-	-	-
AirTemperature1	1側の乾球温度	○	°C	double
AirTemperature2	2側の乾球温度	○	°C	double
Radiation1	1側の放射量	○	W/m2	double
Radiation2	2側の放射量	○	W/m2	double
Incline1	1側の傾斜情報	-	-	-
Incline2	2側の傾斜情報	-	-	-

#### 通常の熱伝導

　壁体の熱伝導を解くにあたっては、壁体表面に入射する放射量と周辺の空気温度が必要となります。AirTemperatureプロパティおよびRadiationプロパティを利用してこれらの情報を入力し、Updateメソッドを呼ぶとTimeStepプロパティに設定された秒数が経過した状態を得ることができます。プログラム内部では、式6.11が後退差分によって解かれ、各壁層の温度が計算されます2)。壁体の質点は図6.12に示されるように各壁層の境界に設けられています。非定常熱伝導を解くプログラムの具体例を図6.13に示します。壁体の構成は表6.19の通りで、3.3.2節で熱回路網を利用して解いたものと同一の構成です。プログラムの実行結果を図6.14と図6.15に示します。回路網を用いた場合とほぼ同様の結果が得られていることが確認できます。

left none {partial T} over {partial t} right rline _m = 1 over {0.5 (CAP_m +CAP_{m+1})} left lbrace 1 over R_{m+1}(T_{m+1} - T_m) - 1 over R_m (T_{m} - T_{m-1}) right rbrace	(6.11)

　T : 壁体温度[°C],　t : 時刻[sec],　M : 壁体分割数,
　CAP : 単位面積あたりの熱容量 [J/(m2K)],　R : 節点間の熱容量 [(m2K)/W]

図6.12　質点の位置

表6.18　Wallクラスの主要メソッド
名称	内容
Update	概要	壁体の状態を更新する
	戻り値	-
	引数1	斜面情報 (ImmutableIncline型)	引数2	1側か否か (bool型)
SetIncline	概要	斜面情報を設定する。裏面は自動で設定される。
	戻り値	-
	引数1	斜面情報 (ImmutableIncline型)	引数2	1側か否か (bool型)
GetSurface	概要	壁表面を取得する
	戻り値	壁表面オブジェクト
	引数1	1側か否か (bool型)	引数2	-
InitializeTemperature	概要	壁体内部の温度を初期化する
	戻り値	-
	引数1	内部の温度 (double型)	引数2	-
SetOverallHeatTransfer / Coefficient	概要	壁表面の総合熱伝達率 [W/(m2 K)]を設定する
	戻り値	-
	引数1	壁表面の総合熱伝達率 (double型)	引数2	1側か否か
SetOverallHeatTransfer / Coefficient	概要	壁表面の総合熱伝達率 [W/(m2 K)]を設定する
	戻り値	-
	引数1	壁表面1の総合熱伝達率 (double型)	引数2	壁表面2の総合熱伝達率 (double型)
GetOverallHeatTransfer / Coefficient	概要	壁表面の総合熱伝達率 [W/(m2 K)]を取得する
	戻り値	壁表面の総合熱伝達率 [W/(m2 K)]
	引数1	1側か否か	引数2	-
SetConvectiveRate	概要	総合熱伝達率[W/m2-K]のうち、対流熱伝達の割合[-]を設定する
	戻り値	-
	引数1	対流熱伝達の割合[-]	引数2	-
SetRadiativeRate	概要	総合熱伝達率[W/m2-K]のうち、放射熱伝達の割合[-]を設定する
	戻り値	-
	引数1	放射熱伝達の割合[-]	引数2	-
GetConvectiveRate	概要	総合熱伝達率[W/m2-K]のうち、対流熱伝達の割合[-]を取得する
	戻り値	対流熱伝達の割合[-]
	引数1	-	引数2	-
GetRadiativeRate	概要	総合熱伝達率[W/m2-K]のうち、放射熱伝達の割合[-]を取得する
	戻り値	放射熱伝達の割合[-]
	引数1	-	引数2	-

表6.19　計算例の壁構成
層番号	素材	熱伝導率 [W/(m K)]	容積比熱 [kJ/(m3 K)]	厚み [mm]
1	合板	0.19	716	25
2	コンクリート	1.4	1934	120
3	空気層	熱抵抗 = 0.086 (m2 K)/W
4	ロックウール	0.042	84	50

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40 / 41 / 42 / 43 / 44 / 45 / 46 / 47	/// <summary>壁熱貫流テスト</summary> / private static void wallHeatTransferTest() / { / WallLayers layers = new WallLayers(); / WallLayers.Layer layer; / layer = new WallLayers.Layer(new WallMaterial("合板", 0.19, 716), 0.025); / layers.AddLayer(layer); / layer = new WallLayers.Layer(new WallMaterial("コンクリート", 1.4, 1934), 0.120); / layers.AddLayer(layer); / layer = new WallLayers.Layer(new WallMaterial("空気層", 1d / 0.086, 0), 0.020); / layers.AddLayer(layer); / layer = new WallLayers.Layer(new WallMaterial("ロックウール", 0.042, 84), 0.050); / layers.AddLayer(layer); / Wall wall = new Wall(layers); / wall.TimeStep = 3600; / wall.AirTemperature1 = 20; / wall.AirTemperature2 = 10; / wall.InitializeTemperature(10); //壁体内温度は10℃均一とする / wall.SurfaceArea = 1; / Console.WriteLine("温度分布の推移"); / Console.WriteLine("合板, コンクリート, 空気層, ロックウール"); / double[] temps; / for (int i = 0; i < 24; i++) / { / wall.Update(); / temps = wall.GetTemperatures(); / Console.Write((i + 1).ToString("F0").PadLeft(2) + "時間後 | "); / for (int j = 0; j < temps.Length - 1; j++) Console.Write(((temps[j] + temps[j + 1]) / 2d).ToString("F1") + " | "); / Console.WriteLine(); / } / //定常状態まで進める / for (int i = 0; i < 1000; i++) wall.Update(); / Console.WriteLine(); / Console.WriteLine("定常状態の温度分布"); / temps = wall.GetTemperatures(); / for (int j = 0; j < temps.Length - 1; j++) Console.Write(((temps[j] + temps[j + 1]) / 2d).ToString("F1") + " | "); / Console.WriteLine(); / Console.WriteLine("定常状態の熱流1: " + wall.GetHeatTransfer(true).ToString("F1")); / Console.WriteLine("定常状態の熱流2: " + wall.GetHeatTransfer(false).ToString("F1")); / Console.WriteLine("定常状態の熱流3: " + wall.GetStaticHeatTransfer().ToString("F1")); / Console.Read(); / }

図6.13　多層壁の熱流計算プログラムの例

温度分布の推移 / 合板, コンクリート, 空気層, ロックウール / 1時間後 | 12.9 | 10.5 | 10.2 | 10.1 | / 2時間後 | 13.7 | 11.0 | 10.5 | 10.3 | / 3時間後 | 14.2 | 11.5 | 10.9 | 10.4 | / 4時間後 | 14.6 | 11.9 | 11.2 | 10.6 | / 5時間後 | 14.9 | 12.3 | 11.6 | 10.9 | / 6時間後 | 15.1 | 12.7 | 12.0 | 11.1 | / 7時間後 | 15.4 | 13.1 | 12.4 | 11.2 | / 8時間後 | 15.6 | 13.4 | 12.7 | 11.4 | / 9時間後 | 15.9 | 13.7 | 13.1 | 11.6 | / 10時間後 | 16.1 | 14.0 | 13.4 | 11.8 | / 11時間後 | 16.2 | 14.3 | 13.6 | 11.9 | / 12時間後 | 16.4 | 14.6 | 13.9 | 12.0 | / 13時間後 | 16.6 | 14.8 | 14.2 | 12.2 | / 14時間後 | 16.7 | 15.0 | 14.4 | 12.3 | / 15時間後 | 16.9 | 15.2 | 14.6 | 12.4 | / 16時間後 | 17.0 | 15.4 | 14.8 | 12.5 | / 17時間後 | 17.2 | 15.6 | 15.0 | 12.6 | / 18時間後 | 17.3 | 15.8 | 15.2 | 12.7 | / 19時間後 | 17.4 | 16.0 | 15.4 | 12.8 | / 20時間後 | 17.5 | 16.1 | 15.5 | 12.9 | / 21時間後 | 17.6 | 16.3 | 15.7 | 13.0 | / 22時間後 | 17.7 | 16.4 | 15.8 | 13.1 | / 23時間後 | 17.8 | 16.5 | 16.0 | 13.1 | / 24時間後 | 17.8 | 16.6 | 16.1 | 13.2 | / 定常状態の温度分布 / 19.0 | 18.3 | 17.8 | 14.1 | / 定常状態の熱流1: 5.9 / 定常状態の熱流2: -5.9 / 定常状態の熱流3: 5.9

図6.14　実行結果

図6.15　壁体内部の温度分布の推移

#### 冷温水配管が埋設されている場合の熱伝導

　壁体内部に冷温水配管を埋設することで壁体を加熱あるいは冷却して、壁表面からの放射によって冷暖房を行う放射冷暖房システムが存在します。このようなシステムを計算する場合には壁体内部に埋め込まれる配管の仕様と、配管が埋設される位置を指定する必要があります。
　配管を表現するクラスとして、Tubeクラスが定義されています。Tubeクラスのコンストラクタを以下に示します。引数はいずれも実数型で、それぞれ、冷温水管埋設層平均温度と冷温水温度との熱通過有効度[-]、フィン効率[-]、流体の比熱[J/(kg K)]を意味しています。これらの値は式6.12~式6.17を利用して求めます。

Tube tube = new Tube(epsilon, finEfficiency, fluidSpecificHeat);

H_P over A_F = {%varepsilon_PNL (c_w G_w)} over A_F (T_wi - T_m)	(6.12)

%varepsilon_PNL = %varepsilon_PX over {1 + (%varepsilon_PX c_w G_w / AC_f) (1/%eta_P - 1)}	(6.13)

%varepsilon_PX = 1 - exp left ( - {{K_P A_F} over {c_w G_w}} right )	(6.14)

"" %eta_P = 1 over w left lbrace D+(w-D) {tanh Z} over Z right rbrace newline "" ~~~~~~ Z={w-D} over 2 sqrt{C_f over {%lambda D}}	(6.15)

K_p = 1 / left lbrace A_F / L left ( 1 / {%pi D %alpha_w} + R_b right ) right rbrace	(6.16)

a_w=1057 (1.352 + 0.0198 T_m) v^0.8 / D^0.2	(6.17)

　HP : 床からの発熱量[W],　AF : 床面積[m3],　cw : 水比熱[J/kg],　Gw : 水流量[kg/s],　Twi : 冷温水温度[°C]
　Tm : 冷温水管埋設層平均温度[°C],　εPNL : 冷温水管埋設層平均温度と冷温水温度との熱通過有効度[-]
　εPX : 管表面と冷温水温度との熱通過有効度[-],　Cf : 冷温水管埋設層から隣接層への熱コンダクタンス[W/(m2 K)]
　ηP : フィン効率[-],　KP : 管表面から冷温水までの熱貫流率[W/(m2 K)],　w : 冷温水管設置間隔[m],　D : 管径[m]
　λ : 床スラブ熱伝導率[W/(m K)],　L : 管の全長[m],　αw : 管内熱伝達率[W/(m2 K)],
　Rb : パネルと管の間の単位管長あたりの熱抵抗 [m K/W],　Tm : 水温[°C],　v : 管内流速 [m/s]

表6.20　Tubeクラスの主要メソッド
名称	内容
SetFlowRate	概要	流体の流量[kg/s]を設定する
	戻り値	-
	引数1	流体の流量[kg/s]	引数2	-
GetOutletFluidTemperature	概要	チューブへの移動熱量[W]を指定して流体の出口温度[C]を計算する
	戻り値	流体の出口温度[C]
	引数1	チューブへの移動熱量[W]	引数2	-
GetOutletFluidTemperature	概要	流体の出口温度[C]を計算する
	戻り値	流体の出口温度[C]
	引数1		引数2	-

　冷温水配管に関連するWallクラスのメソッドを表6.21に示します。AddTubeおよびRemoveTubeメソッドで、作成した冷温水配管オブジェクトを壁体内に埋設します。また、Updateメソッドを呼び出した後、GetHeatTransferToTubeメソッドを使用することで、壁体から冷温水配管へ移動した熱量[W]を計算することができます。

表6.21　Wallクラスの主要メソッド（冷温水配管関連）
名称	内容
AddTube	概要	壁層に冷温水配管を埋め込む
	戻り値	-
	引数1	冷温水配管 (Tube型)	引数2	壁層番号（壁体の分割数を加算した番号）
RemoveTube	概要	壁層から冷温水配管を取り外す
	戻り値	-
	引数1	壁層番号	引数2	-
GetHeatTransferToTube	概要	冷温水配管への熱移動量[W]を計算する
	戻り値	冷温水配管への熱移動量[W]
	引数1	冷温水配管が埋設されている層の番号	引数2	-

　冷温水配管が埋設された床を計算するプログラムの例を図6.17に示します。図6.16に計算対象の床の構成と物性値を示します。熱容量の大きい水パックの間に冷温水配管が埋設されています。

図6.16　計算対象の床の構成と物性値

　配管の素材は架橋ポリエチレンで、設置間隔は267mm、外径は3.4mm、内径は2.3mmです。また、通過水量は0.1L/min/本、加熱する床面積は6.48m2です。フィン効率は以下のように計算できます。
　　Cf = 1 / (0.02 / 0.59) + 1 / (0.02 / 0.59) = 59 W/(m2 K)
　　Z = (0.0267 - 0.0034) × (59 / (0.59 × 0.0034))0.5 = 3.99
　　ηp = 1 / 0.0267 × (0.0034 + (0.0267-0.0037)) × tanh(3.99) / 3.99 = 0.346
　また、架橋ポリエチレンの熱伝導率を0.47 W/(m K)とすると、冷温水管埋設層平均温度と冷温水温度との熱通過有効度[-]は以下のように計算できます。
　　v = (0.01 / 60 / 1000) / (3.14 × (0.0034 / 2)2) = 0.0184 m/s
　　αw = 10.57 × (1.352 + 0.0198 × 25) × 0.01840.8 × 0.00340.2 =235.2
　　Rb = (0.0034 – 0.0023) / (3.14 × 0.47 × 0.0034) = 0.22 m K / W
　　Kp = 1 / (6.48 / 194.4 × (1 / (3.14 × 0.0034 × 235.2) + 0.22)) = 48.6 W/(m2 K)
　　εpx = 1 – exp(-48.6 × 6.48 / 4186 / (0.01 × 54 / 60)) = 0.999
　　εPNL = 0.999 / (1 + 0.999 × 4186 × (0.01 × 54 / 60) / 6.48 / 59) × 1 / 0.34 – 1) = 0.84

　プログラム例の4~16行では、冷温水配管を埋設する壁体を作成しています。18~22行では上記の方法で求めたフィン効率と熱通過有効度を用いて配管オブジェクトを作成し、壁体に設置しています。壁体の計算間隔を300秒とし、100回の繰り返し計算を行い、壁体内部の温度分布の変化を書き出しています。最初の50回は通水量を0とし、50~100回の計算では、0.54L/minで30°Cの温水を通水しています。計算結果を図6.18に示します。通水を行っていない最初の4時間に関しては、壁体内部の温度が外部の温度に近づいていっていることがわかります。通水開始後は温水配管に隣接している壁温度2および壁温度3の温度が大きく上昇し、これに伴って、他の壁体の温度も少しずつ上昇することが確認できます。配管から壁体への熱移動量（GetHeatTransferToTubeメソッドは配管への熱移動を正にとるため、計算結果は負の値）は温度差の大きい通水開始時が最も大きく、2kW程度となっています。

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38	/// <summary>壁熱貫流テスト（冷温水配管埋設）</summary> / private static void wallHeatTransferTest2() / { / WallLayers wl = new WallLayers(); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.FrexibleBoard), 0.0165)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial("水", 0.59, 4186), 0.02)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial("水", 0.59, 4186), 0.02)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.ExtrudedPolystyreneFoam_3), 0.02)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.Plywood), 0.009)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.AirGap), 0.015)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.Plywood), 0.009)); / Wall wall = new Wall(wl); / wall.TimeStep = 300; / wall.AirTemperature1 = 20; / wall.AirTemperature2 = 10; / wall.SurfaceArea = 6.48; / Tube tube = new Tube(0.84, 0.346, 4186); / //配管を埋設 / wall.AddTube(tube, 1); / tube.SetFlowRate(0); //最初は流量0 / tube.FluidTemperature = 30; / wall.InitializeTemperature(20); //壁体温度を初期化 / for (int i = 0; i < wall.Layers.LayerNumber; i++) Console.Write("温度" + i + ", "); / Console.WriteLine("配管への熱移動量[W], 配管出口温度[C]"); / for (int i = 0; i < 100; i++) / { / if (i == 50) tube.SetFlowRate(0.54); //通水開始 / wall.Update(); / double[] tmp = wall.GetTemperatures(); / for (int j = 0; j < tmp.Length - 1; j++) Console.Write(((tmp[j] + tmp[j + 1]) / 2d).ToString("F1") + ", "); / Console.Write(wall.GetHeatTransferToTube(1).ToString("F0") + ", " + tube.GetOutletFluidTemperature().ToString("F1")); / Console.WriteLine(); / } / Console.Read(); / }

図6.17　冷温水配管埋設壁の熱貫流計算プログラムの例

図6.18　壁体内部の温度分布の推移（4:10に通水開始）

#### 潜熱蓄熱材料がある場合の熱伝導

　凝固熱や融解熱など、相変化に伴う熱移動を利用して大きな蓄熱を行うことができる材料を相変化材料（PCM : Phase Change Materials）と呼びます。相変化の前後で熱伝導率や容積比熱が変化するため、PCMが含まれた壁体の計算を行う場合には、相変化材料に関する特別な設定が必要となります。
　PCMを表現するためにはLatentHeatStorageMaterialクラスを使用します。PCMは、温度に応じて相が変化し、それぞれの相で熱伝導率と容積比熱が異なります。そこで、異なる物性を持ったWallMaterialオブジェクトを作成した後、温度区分とともにLatentHeatStorageMaterialオブジェクトに設定します。概念を図6.19に示します。

図6.19　PCMの温度区分に応じたWallMaterialオブジェクトの設定

　LatentHeatStorageMaterialクラスのコンストラクタは以下の通りです。第二引数は、壁体の材料を表すImmutableWallMaterial型のオブジェクトです。このオブジェクトの物性値は、第一引数で与えられた上限温度まで適用されます。

LatentHeatStorageMaterial lmat = new LatentHeatStorageMaterial(upperTemperature, material);

　主要なメソッドを表6.22に示します。

表6.22　LatentHeatStorageMaterialクラスの主要メソッド
名称	内容
AddMaterial	概要	壁材料を追加する
	戻り値	-
	引数1	温度上限 [C]	引数2	壁材料
GetMaterial	概要	指定された温度の時の材料物性を取得する
	戻り値	指定された温度の時の材料物性 (ImmutableWallMaterial型)
	引数1	温度	引数2	-
Initialize	概要	指定された温度に初期化する
	戻り値	-
	引数1	温度	引数2	-
GetHeatStorage	概要	温度1から温度2に変化した場合の蓄熱量[kJ/m3]を計算する
	戻り値	温度1から温度2に変化した場合の蓄熱量[kJ/m3]
	引数1	温度1	引数2	温度2

　作成したLatentHeatStorageMaterialオブジェクトを壁体に設定するためには、表6.23に示すWallクラスのメソッドを使用します。SetLatentHeatStorageMaterialメソッドで潜熱蓄熱材料を壁体に設定し、RemoveLatentHeatStorageMaterialメソッドで設定を解除します。

表6.23　Wallクラスの主要メソッド（潜熱蓄熱材設定関連）
名称	内容
SetLatentHeat / StorageMaterial	概要	潜熱蓄熱材料を設定する
	戻り値	-
	引数1	壁層番号	引数2	潜熱蓄熱材 (LatentHeatStorageMaterial型)
RemoveLatentHeat / StorageMaterial	概要	潜熱蓄熱材料の設定を解除する
	戻り値	-
	引数1	壁層番号	引数2	-

　図6.21に、潜熱蓄熱材を含む壁体の非定常熱伝導を計算するプログラムの例を示します。2)で作成した壁体とほぼ同様の構成とし、第二層と第三層の水パックを潜熱蓄熱材で置き換えました。第二層と第三層に設定した潜熱蓄熱材の物性を表6.24に示します。

表6.24　潜熱蓄熱材の物性
層番号	温度区分 [°C]	状態	容積比熱 [kJ/(m3-K)]	熱伝導率 [W/(m-K)]
第二層	~19	固相	5040	0.19
	19~23	転移相	21140	0.205
	23~	液相	5040	0.22
第三層	~30	固相	5004	0.19
	30~32	転移相	88550	0.205
	32~	液相	4935	0.22

　プログラム例では、24~38行目で表6.24の潜熱蓄熱材料を作成し、壁体に設定しています。最初は配管に通水を行わず、初期温度の35°Cから壁体を冷却していきます。100タイムステップ経過後に通水を開始するとともに壁体周囲の温度を30°Cに上げ、壁体を加熱しています。各タイムステップでは、壁体内部の各層の温度と、初期温度と比較した蓄熱量を書き出しています。
　図6.20に計算結果を示します。波線が第三層に設置された潜熱蓄熱材の温度で、冷却時および加熱時ともに、転移相となる30~32°Cで非線形に温度変化が生じていることがわかります。また、この影響を受けて他の壁層でも温度変化が変曲していることが確認できます。

図6.20　計算結果

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40 / 41 / 42 / 43 / 44 / 45 / 46 / 47 / 48 / 49 / 50 / 51 / 52 / 53 / 54 / 55 / 56 / 57 / 58 / 59 / 60 / 61 / 62 / 63 / 64 / 65 / 66	/// <summary>壁熱貫流テスト（潜熱蓄熱材）</summary> / private static void wallHeatTransferTest3() / { / //初期温度 / const double INIT_TEMP = 35; / //壁層を作成 / WallLayers wl = new WallLayers(); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.FrexibleBoard), 0.0165)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial("ダミー材料", 1, 1), 0.02)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial("ダミー材料", 1, 1), 0.02)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.ExtrudedPolystyreneFoam_3), 0.02)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.Plywood), 0.009)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.AirGap), 0.015)); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.Plywood), 0.009)); / //壁体を作成 / Wall wall = new Wall(wl); / wall.TimeStep = 1200; / wall.AirTemperature1 = 20; / wall.AirTemperature2 = 20; / wall.SurfaceArea = 6.48; / //潜熱蓄熱材1を作成して設定 / LatentHeatStorageMaterial material1; / material1 = new LatentHeatStorageMaterial(19, new WallMaterial("パッシブ・スミターマル（凝固）", 0.19, 3.6 * 1400)); / material1.AddMaterial(23, new WallMaterial("パッシブ・スミターマル（遷移）", (0.19 + 0.22) / 2d, 15.1 * 1400)); / material1.AddMaterial(100, new WallMaterial("パッシブ・スミターマル（融解）", 0.22, 3.6 * 1400)); / material1.Initialize(INIT_TEMP); / wall.SetLatentHeatStorageMaterial(1, material1); / //潜熱蓄熱材2を作成して設定 / LatentHeatStorageMaterial material2; / material2 = new LatentHeatStorageMaterial(30, new WallMaterial("スミターマル（凝固）", 0.19, 3.6 * 1390)); / material2.AddMaterial(32, new WallMaterial("スミターマル（遷移）", (0.19 + 0.22) / 2d, 63.25 * 1400)); / material2.AddMaterial(100, new WallMaterial("スミターマル（融解）", 0.22, 3.5 * 1410)); / material2.Initialize(INIT_TEMP); / wall.SetLatentHeatStorageMaterial(2, material2); / //潜熱蓄熱材の間に配管を埋設 / Tube tube = new Tube(0.84, 0.346, 4186); / wall.AddTube(tube, 1); / tube.SetFlowRate(0); / tube.FluidTemperature = 40; / //壁体温度を初期化 / wall.InitializeTemperature(INIT_TEMP); / for (int i = 0; i < wall.Layers.LayerNumber; i++) Console.Write("温度" + i + ", "); / Console.WriteLine("蓄熱量[kJ]"); / for (int i = 0; i < 200; i++) / { / if (i == 100) / { / tube.SetFlowRate(0.54); //通水開始 / wall.AirTemperature1 = 30; / wall.AirTemperature2 = 30; / } / wall.Update(); / double[] tmp = wall.GetTemperatures(); / for (int j = 0; j < tmp.Length - 1; j++) Console.Write(((tmp[j] + tmp[j + 1]) / 2d).ToString("F1") + ", "); / Console.Write(wall.GetHeatStorage(INIT_TEMP).ToString("F0")); / Console.WriteLine(); / } / Console.Read(); / }

図6.21　潜熱蓄熱材を含む壁体の非定常熱伝導を計算するプログラム例

### 室の温湿度変動計算に関するクラス

　本クラスライブラリでは、室の温湿度変動を計算するために、Zoneクラス、Roomクラス、MultiRoomクラス、Outdoorクラス、IHeatGarinインターフェース、ISurfaceインターフェースを用意しています。図6.22に各クラスおよびインターフェースの概念を示します。
　Roomクラスは壁面や窓面に囲まれた領域を表現しています。この領域が均一でなく、一部で性状が異なる場合（例えばインテリアゾーン、ペリメータゾーンなど）、Zoneクラスを利用して領域を分割することができます。Zoneクラスで表現された領域は完全混合であるとみなされ、1つの空気状態（MoistAir型オブジェクト）で代表されます。また、Zoneに属する熱負荷発生源はIHeatGainインターフェースで表現します。Roomクラスに面している壁の表面や窓の表面を表現するためにはISurfaceクラスを利用します。壁表面の反対側は屋外の場合もありますが、別のRoomが続いている可能性もあります。このように、壁体を挟んで連続する2以上のRoomをまとめて取り扱うためのクラスがMultiRoomクラスです。一方、屋外を特徴付ける要素として太陽位置や外気状態がありますが、これらをまとめて取り扱うクラスとしてOutdoorクラスが定義されています。
　これらの内、ZoneクラスまたはMultiRoomクラスに定義しているUpdateメソッドを利用することで室温変動を解くことができます。両者の違いは、どの範囲までを連成させるかにあります。各ゾーンの温度はそのゾーンを囲む壁体の温度に依存します。しかし、これらの壁体の温度は、壁の反対側に存在する別のゾーンの温度や、そのゾーンに含まれる別の壁表面の温度に依存しています。また、室間換気量がある場合には、各ゾーンの空気状態は相互に影響を与えます。従って、厳密に連成を行い、熱収支を合わせるためには全ての壁表面の温度、ゾーンの温湿度を同時に解く必要があります。この場合にはMultiRoomクラスのUpdateメソッドを利用します。一方で簡易化のために、壁の反対側のゾーンの相当温度を境界条件（例えば1タイムステップ前の状態値を与えておくなど）として計算を行うという方法も考えられます。この場合には、ZoneクラスのUpdateメソッドを利用します。

図6.22　潜熱蓄熱材を含む壁体の非定常熱伝導を計算するプログラム例

　以下に計算サンプルの建物の仕様と、ZoneクラスおよびMultiRoomクラスを利用して計算を行う方法を示します。

#### 計算対象の建物

　図6.23に計算対象の建物の平面図と断面図を示します。南側に窓を持つ直方体の室が東西に2つ連続したした、単純な形状の建物です。東側の室の窓には庇が設けられており、室内には発熱体が設置されています。庇の横幅は5m、張り出しは1mとし、窓の0.5m上方に設置されています。窓からの奥行きは7mですが、窓側3mをペリメータゾーンとし、それ以外の領域をインテリアゾーンとして区別します。西側の室は10CMHで外気が取り入れられていますが、ペリメータ側から給気し、インテリア側から排気することとします。東側の室では外気を取り入れず、ペリメータとインテリアで10CMHでゾーン間換気を行うこととします。南面窓はLow-Eの二重ガラスとし、大きさは3m×2mとします。壁体は、内壁、外壁ともに400mmのコンクリートとします。単純化のため、基礎は考慮せず、建物は地面に直接に置かれていることとし、地中温度は25°Cで一定に保たれることとします。
　表6.25、図6.24、図6.25に、外界条件として利用する気象データを示します。2007年8月3日に東京で観測された値です。
　空調時間帯は8:00~19:00とし、無限大の容量を持つ空調機によって、乾球温度は26°C、絶対湿度は0.01kg/kg(DA) に保たれることとします。

図6.23　計算対象建物の平面図と断面図

表6.25　計算用気象データ（東京：2007年8月3日）
時刻	乾球温度[℃]	絶対湿度[kg/kg(DA)]	夜間放射[W/m2]	法線面直達日射[W/m2]	水平面天空日射[W/m2]
0:00	24.2	0.0134	32	0	0
1:00	24.1	0.0136	30	0	0
2:00	24.1	0.0134	30	0	0
3:00	24.2	0.0133	29	0	0
4:00	24.3	0.0131	26	0	0
5:00	24.2	0.0134	24	0	0
6:00	24.4	0.0138	24	106	36
7:00	25.1	0.0142	25	185	115
8:00	26.1	0.0142	25	202	198
9:00	27.1	0.0140	25	369	259
10:00	28.8	0.0147	24	427	314
11:00	29.9	0.0149	24	499	340
12:00	30.7	0.0142	24	557	340
13:00	31.2	0.0146	23	522	349
14:00	31.6	0.0140	24	517	319
15:00	31.4	0.0145	24	480	277
16:00	31.3	0.0144	24	398	228
17:00	30.8	0.0146	24	255	167
18:00	29.4	0.0142	23	142	87
19:00	28.1	0.0136	23	2	16
20:00	27.5	0.0136	24	0	0
21:00	27.1	0.0135	26	0	0
22:00	26.6	0.0136	25	0	0
23:00	26.3	0.0140	23	0	0

図6.24　気象データ（乾球温度・絶対湿度）

図6.25　気象データ（日射・夜間放射）

#### Zoneクラスを利用して解く方法

　Zoneクラスを利用すると、式6.18および式6.19で表現される室内空気の顕熱平衡式および潜熱平衡式†[1])を解くことができます2) [18])。式6.18で表現される数式モデルの大きな特徴は右辺第一項にあります。厳密にはゾーンに面する窓や壁体の表面温度はそれぞれに異なりますが、本式では、平均の表面温度であるTMRTで一定として取り扱っています。また、表面とゾーンとの間の総合熱伝達率の対流成分も異なりますが、本式ではα(i) kcで一定としています。
[1] 参考文献2)の宇田川の式に水蒸気容量の項を加えた
[18] 松尾陽 : 空調負荷計算におけるふく射伝熱の扱い, 空気調和・衛生工学, 59-4, 1985, pp.323~329

ZN_S {d T_R} over {dt} = sum from n=1 to NW A_n %alpha_(i) k_c (T_MRT - T_R) + c_a G_o (T_a - T_R) + HG_(c) - HE_s	(6.18)

ZN_S = c_a %rho cdot VOL + CPF	(6.19)

ZN_L {d x_R} over {dt} = G_o (x_a - x_R) + LG - %LE	(6.20)

ZN_L = %rho cdot VOL + LCPF	(6.21)

　ZNS : ゾーンの顕熱容量 [J/K],　TR : ゾーンの乾球温度 [°C],　t : 時間 [sec],　NW : ゾーンに含まれる表面の数,　An : 表面積 [m2]
　α(i) : 総合熱伝達率 [W/(m2 K)],　kc : 総合熱伝達率の対流比率 [-],　TMRT : 周壁の平均温度 [°C],　ca : 空気の比熱 [J/(kg K)]
　Go : 換気量 [kg/s],　Ta : 外気の乾球温度 [°C],　HG(c) : 室内発生顕熱の対流成分 [W],　HEs : 室への供給熱量 [W]
　ρ : 空気の密度 [kg/m3],　VOL : 室容積 [m3],　CPF : 家具などの熱容量 [J/K]
　ZNL : ゾーンの水蒸気容量 [kg],　xR : ゾーンの絶対湿度 [kg/kg(DA)],　xa : 外気の絶対湿度 [kg/kg(DA)],
　LG : ゾーン内発生水蒸気量 [kg/s],　LE : 水蒸気除去量 [kg/s],　LCPF : 家具などの水蒸気容量 [kg]

　Zoneクラスの主要なプロパティとメソッドを表6.26と表6.27に示します。
　SensibleHeatCapacityは空気以外の顕熱容量であり、家具などの熱容量です (上式のCPF)。オフィスの場合は単位容積あたりで12~15 kJ/(m3 K) [19]) [20])、住宅の場合はその半分程度の値となります。
[19] 木村建一, 伊藤直明 : 事務所建築の家具の熱容量, 日本建築学会関東支部第29会研究発表会, 1961-1, 同続報, 同第34回, 1963-5
[20] 石野久彌, 郡公子 : 事務所建築における家具類の熱的影響に関する実測・実験研究, 日本建築学会計画系論文報告集 (372), 59-66, 1987, 0228
　LatentHeatCapacityは空気以外の水蒸気容量であり、家具などの水蒸気容量です (上式のLCPF)。家具や壁体の吸放湿を無視するのであれば0としておきます†[2])。
[2] 松尾陽 : 室の潜熱容量について, 日本建築学会大会学術講演梗概集, 1987, 等を参照して下さい。
　HeatTransferCoefficientはゾーンに属する壁や窓の表面の総合熱伝達率で、Zoneクラスを利用して計算を行う場合にはすべての表面が同一の値をとると仮定します (上式のα(i))。また、kcを設定するためにはSetConvectiveRateメソッドを使用します。
　式6.18または式6.19をTrまたはxRについて解けば室の乾球温度または絶対湿度が求まり、HEsまたはLEについて解けば顕熱負荷または潜熱負荷が求まります。これらの切り替えを行うためには、ControlDrybulbTemperatureまたはControlAbusoluteHumidityの設定を変更します。trueに設定すると、乾球温度または絶対湿度が、DrybulbTemperatureSetPointまたはAbsoluteHumiditySetPointに指定された値で一定に保たれ、負荷が計算されます。falseに設定した場合には、SensibleHeatSupplyとLatentHeatSupplyで設定された供給顕熱量と供給潜熱量を所与として、乾球温度または絶対湿度が変動することになります。
　AtmosphericPressureは大気圧で、空気の密度に影響を与えます。SurfacesとHeatGainsはそれぞれ、室に面している壁や窓の表面リストと室内発熱要素のリストです。これらはAddSurfaceやAddHeatGainメソッド等を利用して設定します。

表6.26　Zoneクラスの主要なプロパティ一覧
プロパティ名称	内容	setアクセッサ	単位	型
TimeStep	計算時間間隔	○	sec	double
Name	室名称	○	-	string
Volume	室容積	○	m3	double
SensibleHeatCapacity	空気以外の顕熱容量[J/K]	○	J/K	double
SensibleHeatSupply	顕熱供給[W]（暖房を正とする）	○	W	double
LatentHeatCapacity	空気以外の水蒸気容量[kg]	○	kg	double
LatentHeatSupply	潜熱供給[W]（加湿を正とする）	○	W	double
HeatTransferCoefficient	室に属する壁窓面の総合熱伝達率	○	W/(m2 K)	double
VentilationVolume	換気量	○	m3/h	double
VentilationAirState	換気空気状態	○	-	MoistAir
ControlDrybulbTemperature	乾球温度を制御するか否か	○	-	bool
ControlAbsoluteHumidity	絶対湿度を制御するか否か	○	-	bool
DrybulbTemperatureSetPoint	乾球温度設定値	○	°C	double
AbsoluteHumiditySetPoint	絶対湿度設定値	○	kg/kg(DA)	dobule
Surfaces	室に面している壁窓面リスト	-	-	ImmutableSurface[ ]
HeatGains	室内発熱要素リスト	-	-	IheatGain[ ]
AtmosphericPressure	大気圧	○	kPa	double
CurrentDrybulbTemperature	現在の乾球温度	-	°C	double
CurrentAbsoluteHumidity	現在の絶対湿度	-	kg/kg(DA)	double
CurrentSensibleHeatLoad	現在の顕熱負荷	-	W	double
CurrentLatentHeatLoad	現在の潜熱負荷	-	W	double
CurrentMeanRadiantTemperature	現在の平均放射温度	-	°C	double
CurrentDateTime	現在の日時	○	-	DateTime

表6.27　Zoneクラスの主要なメソッド一覧
名称	内容
AddSurface	概要	表面を追加する
	戻り値	追加成功の真偽
	引数1	追加する表面 (ISurface型)	引数2	-
RemoveSurface	概要	表面を削除する
	戻り値	削除成功の真偽
	引数1	削除する表面 (ISurface型)	引数2	-
AddWindow	概要	窓を追加する
	戻り値	追加成功の真偽
	引数1	追加する窓 (Window型)	引数2	-
RemoveWindow	概要	窓を削除する
	戻り値	削除成功の真偽
	引数1	削除する窓 (Window型)	引数2	-
AddHeatGain	概要	発熱要素を追加する
	戻り値	追加成功の真偽
	引数1	追加する発熱要素 (IHeatGain型)	引数2	-
RemoveHeatGain	概要	発熱要素を削除する
	戻り値	削除成功の真偽
	引数1	削除する発熱要素 (IHeatGain型)	引数2	-
SetConvectiveRate	概要	総合熱伝達率[W/(m2 K)]のうち、対流熱伝達の割合[-]を設定する
	戻り値	-
	引数1	対流熱伝達の割合[-]	引数2	-
InitializeAirState	概要	温湿度を初期化する
	戻り値	-
	引数1	乾球温度 [°C]	引数2	絶対湿度 [kg/kg(DA)]

　Zoneクラスのモデル更新関連のメソッド一覧を表6.28に示します。Updateメソッドを使用すると、TimeStepで指定した秒数が経過した後の室の状態を計算することができます。また、GetNext~~という名称のメソッドを利用すると、状態を更新させずにTimeStep経過後の室の各種状態値を取得することができます。

表6.28　Zoneクラスのモデル更新関連のメソッド一覧
名称	内容
Update	概要	TimeStepで設定された秒数を経過させ、状態を更新する
	戻り値	-
	引数1	-	引数2	-
GetNextDrybulbTemperature	概要	指定された顕熱供給[W]があった場合の室の乾球温度[°C]を計算する
	戻り値	室の乾球温度[°C]
	引数1	顕熱供給[W]（暖房を正とする）	引数2	-
GetNextAbsoluteHumidity	概要	指定された潜熱供給[W]があった場合の室の絶対湿度[kg/kg(DA)]を計算する
	戻り値	室の絶対湿度[kg/kg(DA)]
	引数1	潜熱供給[W]（加湿を正とする）	引数2	-
GetNextMeanRadiantTemperature	概要	現在の設定が継続した場合の、次タイムステップの周壁平均温度[°C]を計算する
	戻り値	次タイムステップの周壁平均温度[°C]
	引数1	-	引数2	-
GetNextSensibleHeatLoad	概要	指定された室乾球温度[°C]を達成するための顕熱供給[W]を計算する
	戻り値	顕熱供給[W]
	引数1	室乾球温度[°C]	引数2	-
GetNextLatentHeatLoad	概要	指定された室絶対湿度[kg/kg(DA)]を達成するための潜熱供給[W]を計算する
	戻り値	潜熱供給[W]
	引数1	絶対湿度[kg/kg(DA)]	引数2	-

　ゾーンに面する壁や窓の表面近傍の相当温度は式6.22上段で表現されます。一方、屋外に面する壁や窓の表面近傍の相当温度は式6.22中段または下段で表現されます。中段は空気に面している場合、下段は地面に接する場合です。中段および下段の式を一括して計算するために、Outdoorクラスが用意されています。
　Outdoorクラスのプロパティ一覧とメソッド一覧をを表6.29と表6.30に示します。Add~~という名称のメソッドとRemove~~という名称のメソッドを使用することで外表面を追加および削除することができます。その後、AirState、Sun、GroundTemperature、NocturnalRadiationプロパティに屋外の状態を設定し、SetWallSurfaceBoundaryStateメソッドを呼び出すと、登録された外表面に式6.22に相当する情報が設定されます。

T_SOL = left lbrace stack{ "" {a_(c) T_R + a_(r) T_MRT + RS} over a_(i) # "" {a_s I_W - %varepsilon F_S RN} over %alpha_o + T_a # "" T_GRZ } right none	(6.22)

　TSOL : 壁や窓表面近傍の相当温度 [°C],　TR : ゾーンの乾球温度 [°C],　TMRT : 周壁の平均温度 [°C],　RS : 表面への放射 [W/m2]
　α(i) : 総合熱伝達率 [W/(m2 K)],　α(c) : 対流熱伝達率 [W/(m2 K)],　α(r) : 放射熱伝達率 [W/(m2 K)]
　as : 日射吸収率 [-],　IW : 日射 [W/m2],　ε : 放射率 [-],　FS : 外表面から天空への形態係数 [-],　RN : 夜間放射 [W/m2]
　Ta : 外気乾球温度 [°C],　TGRZ : 地中温度 [°C]

表6.29　Outdoorクラスの主要なプロパティ一覧
プロパティ名称	内容	setアクセッサ	単位	型
AirState	屋外の空気状態	○	-	MoistAir
Sun	太陽の情報	○	-	Sun
WallSurfaces	空気に面している壁表面リスト	○	-	ImmutableWallSurface []
GroundWallSurfaces	地面に接する壁表面リスト	-	-	ImmutableWallSurface []
Windows	窓リスト	-	-	ImmutableWindow []
GroundTemperature	地中温度	○	°C	double
NocturnalRadiation	夜間放射	○	W/m2	double

表6.30　Outdoorクラスのメソッド一覧
名称	内容
SetWallSurfaceBoundaryState	概要	登録されている壁表面の境界条件を設定する
	戻り値	-
	引数1	-	引数2	-
AddWallSurface	概要	空気に面した壁表面を追加する
	戻り値	追加成功の真偽
	引数1	追加する壁表面(WallSurface型)	引数2	-
RemoveWallSurface	概要	空気に面した壁表面を削除する
	戻り値	削除成功の真偽
	引数1	削除する壁表面(WallSurface型)	引数2	-
AddGroundWallSurface	概要	地面に面した壁表面を追加する
	戻り値	追加成功の真偽
	引数1	追加する壁表面(WallSurface型)	引数2	-
RemoveGroundWallSurface	概要	地面に面した壁表面を削除する
	戻り値	削除成功の真偽
	引数1	削除する壁表面(WallSurface型)	引数2	-
AddWindow	概要	窓を追加する
	戻り値	追加成功の真偽
	引数1	追加する窓 (Window型)	引数2	-
RemoveWindow	概要	窓を削除する
	戻り値	削除成功の真偽
	引数1	削除する窓 (Window型)	引数2	-
GetRadiationToIncline	概要	斜面に入射する放射量[W/m2]を計算する
	戻り値	斜面に入射する放射量[W/m2]
	引数1	斜面 (Incline型)	引数2	アルベド [-]
	引数3	日影率 [-]	引数4	-
SetConvectiveRate	概要	登録された壁表面の対流熱伝達の比率を設定する
	戻り値	-
	引数1	対流熱伝達の比率	引数2	-
SetOverallHeatTransferCoefficient	概要	表面の総合熱伝達率[W/(m2 K)]を設定する
	戻り値	-
	引数1	総合熱伝達率[W/(m2 K)]	引数2	対流熱伝達の比率

　Zoneクラスを利用して1)で説明した多数室の計算を行うプログラムの例を図6.28に示します。
　全体の大きな流れは以下の通りです。

1) 壁体(Wall)と窓(Window)を作成する
2) 壁体表面(WallSurface)と窓(Window)をゾーン(Zone)と屋外(Outdoor)に関連づける
3) 屋外の状態を更新する
4) 屋外の状態を登録された表面に設定する
5) 壁体を更新する
6) ゾーンを更新する
7) ゾーンの状態を壁表面に設定する
8) 3)に戻る

　4~11行では気象データを実数値配列に代入しています。14~17行では屋外を表現するOutdoorオブジェクトを作成しており、太陽は東京で初期化しています。20~24行では、壁表面や窓表面の向きを指定するために必要な傾斜面オブジェクトを作成しています。26~42行は、ゾーンオブジェクトの作成処理です。48, 49行目で作成した壁体の構成を利用し、54~166行で壁体を作成しています。また、GetSurfaceメソッドを使用して壁体表面オブジェクトを取得し、ゾーンまたは屋外オブジェクトに設定を行っています。同様に、52行で作成した窓構成を利用し、169~178行で窓の作成および室への設定を行っています。180~240行は計算の実行と書き出し処理です。定常状態になるように同一気象データで100回の繰り返し計算を行い、100回目に書き出しを行っています。
　本プログラムを実行した結果を図6.26と図6.27に示します。空調時間帯の8:00~19:00は乾球温度が一定となっており、顕熱負荷が計上されていることがわかります。空調開始時の8:00は相対的に負荷が大きくなっていますが、外気を導入している西側ペリメータに関しては外気温度の変化に合わせて負荷が上昇していることが確認できます。

図6.26　乾球温度の推移

図6.27　顕熱負荷の推移

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40 / 41 / 42 / 43 / 44 / 45 / 46 / 47 / 48 / 49 / 50 / 51 / 52 / 53 / 54 / 55 / 56 / 57 / 58 / 59 / 60 / 61 / 62 / 63 / 64 / 65 / 66 / 67 / 68 / 69 / 70 / 71 / 72 / 73 / 74 / 75 / 76 / 77 / 78 / 79 / 80 / 81 / 82 / 83 / 84 / 85 / 86 / 87 / 88 / 89 / 90 / 91 / 92 / 93 / 94 / 95 / 96 / 97 / 98 / 99 / 100 / 101 / 102 / 103 / 104 / 105 / 106 / 107 / 108 / 109 / 110 / 111 / 112 / 113 / 114 / 115 / 116 / 117 / 118 / 119 / 120 / 121 / 122 / 123 / 124 / 125 / 126 / 127 / 128 / 129 / 130 / 131 / 132 / 133 / 134 / 135 / 136 / 137 / 138 / 139 / 140 / 141 / 142 / 143 / 144 / 145 / 146 / 147 / 148 / 149 / 150 / 151 / 152 / 153 / 154 / 155 / 156 / 157 / 158 / 159 / 160 / 161 / 162 / 163 / 164 / 165 / 166 / 167 / 168 / 169 / 170 / 171 / 172 / 173 / 174 / 175 / 176 / 177 / 178 / 179 / 180 / 181 / 182 / 183 / 184 / 185 / 186 / 187 / 188 / 189 / 190 / 191 / 192 / 193 / 194 / 195 / 196 / 197 / 198 / 199 / 200 / 201 / 202 / 203 / 204 / 205 / 206 / 207 / 208 / 209 / 210 / 211 / 212 / 213 / 214 / 215 / 216 / 217 / 218 / 219 / 220 / 221 / 222 / 223 / 224 / 225 / 226 / 227 / 228 / 229 / 230 / 231 / 232 / 233 / 234 / 235 / 236 / 237 / 238 / 239 / 240 / 241	/// <summary>室の温湿度変動テスト(Zoneクラス)</summary> / private static void RoomModelTest1() / { / //気象データ:乾球温度,絶対湿度,夜間放射,直達日射,天空日射 / double[] dbt = new double[] { 24.2, 24.1, 24.1, 24.2, 24.3, 24.2, 24.4, 25.1, 26.1, 27.1, 28.8, 29.9, / 30.7, 31.2, 31.6, 31.4, 31.3, 30.8, 29.4, 28.1, 27.5, 27.1, 26.6, 26.3 }; / double[] ahd = new double[] { 0.0134, 0.0136, 0.0134, 0.0133, 0.0131, 0.0134, 0.0138, 0.0142, 0.0142, 0.0140, 0.0147, 0.0149, / 0.0142, 0.0146, 0.0140, 0.0145, 0.0144, 0.0146, 0.0142, 0.0136, 0.0136, 0.0135, 0.0136, 0.0140 }; / double[] nrd = new double[] { 32, 30, 30, 29, 26, 24, 24, 25, 25, 25, 24, 24, 24, 23, 24, 24, 24, 24, 23, 23, 24, 26, 25, 23 }; / double[] dnr = new double[] { 0, 0, 0, 0, 0, 0, 106, 185, 202, 369, 427, 499, 557, 522, 517, 480, 398, 255, 142, 2, 0, 0, 0, 0 }; / double[] drd = new double[] { 0, 0, 0, 0, 0, 0, 36, 115, 198, 259, 314, 340, 340, 349, 319, 277, 228, 167, 87, 16, 0, 0, 0, 0 }; / //屋外を作成 / Outdoor outdoor = new Outdoor(); / Sun sun = new Sun(Sun.City.Tokyo); / outdoor.Sun = sun; / outdoor.GroundTemperature = 25; / //傾斜を作成 / Incline nIn = new Incline(Incline.Orientation.N, 0.5 * Math.PI); //北 / Incline eIn = new Incline(Incline.Orientation.E, 0.5 * Math.PI); //東 / Incline wIn = new Incline(Incline.Orientation.W, 0.5 * Math.PI); //西 / Incline sIn = new Incline(Incline.Orientation.S, 0.5 * Math.PI); //南 / Incline hIn = new Incline(Incline.Orientation.S, 0); //水平 / //ゾーンを作成 / Zone[] zones = new Zone[4]; / Zone wpZone = zones[0] = new Zone("西室ペリメータ"); / wpZone.Volume = 3 * 5 * 3; / Zone wiZone = zones[1] = new Zone("西室インテリア"); / wiZone.Volume = 4 * 5 * 3; / Zone epZone = zones[2] = new Zone("東室ペリメータ"); / epZone.Volume = 3 * 5 * 3; / Zone eiZone = zones[3] = new Zone("東室インテリア"); / eiZone.Volume = 4 * 5 * 3; / foreach (Zone zn in zones) / { / zn.VentilationVolume = 10; //換気量[CMH](ゾーン間換気もこのプロパティを援用する) / zn.TimeStep = 3600; / zn.DrybulbTemperatureSetPoint = 26; / zn.AbsoluteHumiditySetPoint = 0.01; / } / //東側インテリアに発熱体を設定 / eiZone.AddHeatGain(new ConstantHeatGain(100, 100, 20)); / //壁構成を作成:400mmコンクリート / WallLayers wl = new WallLayers(); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.ReinforcedConcrete), 0.4)); / //窓構成を作成 / GlassPanes gPanes = new GlassPanes(new GlassPanes.Pane(GlassPanes.Pane.PredifinedGlassPane.HeatReflectingGlass06mm)); / //壁体をゾーンに追加 / Wall[] walls = new Wall[18]; / List<WallSurface> outdoorSurfaces = new List<WallSurface>(); / Wall wpwWall = walls[0] = new Wall(wl, "西室ペリメータ西壁"); / wpwWall.SurfaceArea = 3 * 3; / outdoorSurfaces.Add(wpwWall.GetSurface(true)); / wpZone.AddSurface(wpwWall.GetSurface(false)); / wpwWall.SetIncline(wIn, true); / Wall wpcWall = walls[1] = new Wall(wl, "西室ペリメータ天井"); / wpcWall.SurfaceArea = 3 * 5; / outdoorSurfaces.Add(wpcWall.GetSurface(true)); / wpZone.AddSurface(wpcWall.GetSurface(false)); / wpcWall.SetIncline(hIn, true); / Wall wpfWall = walls[2] = new Wall(wl, "西室ペリメータ床"); / wpfWall.SurfaceArea = 3 * 5; / outdoor.AddGroundWallSurface(wpfWall.GetSurface(true)); / wpZone.AddSurface(wpfWall.GetSurface(false)); / Wall winWall = walls[3] = new Wall(wl, "西室インテリア北壁"); / winWall.SurfaceArea = 3 * 5; / outdoorSurfaces.Add(winWall.GetSurface(true)); / wiZone.AddSurface(winWall.GetSurface(false)); / winWall.SetIncline(nIn, true); / Wall wiwWall = walls[4] = new Wall(wl, "西室インテリア西壁"); / wiwWall.SurfaceArea = 3 * 4; / outdoorSurfaces.Add(wiwWall.GetSurface(true)); / wiZone.AddSurface(wiwWall.GetSurface(false)); / wiwWall.SetIncline(wIn, true); / Wall wicWall = walls[5] = new Wall(wl, "西室インテリア天井"); / wicWall.SurfaceArea = 4 * 5; / outdoorSurfaces.Add(wicWall.GetSurface(true)); / wiZone.AddSurface(wicWall.GetSurface(false)); / wicWall.SetIncline(hIn, true); / Wall wifWall = walls[6] = new Wall(wl, "西室インテリア床"); / wifWall.SurfaceArea = 4 * 5; / outdoor.AddGroundWallSurface(wifWall.GetSurface(true)); / wiZone.AddSurface(wifWall.GetSurface(false)); / Wall epwWall = walls[7] = new Wall(wl, "東室ペリメータ東壁"); / epwWall.SurfaceArea = 3 * 3; / outdoorSurfaces.Add(epwWall.GetSurface(true)); / epZone.AddSurface(epwWall.GetSurface(false)); / epwWall.SetIncline(eIn, true); / Wall epcWall = walls[8] = new Wall(wl, "東室ペリメータ天井"); / epcWall.SurfaceArea = 3 * 5; / outdoorSurfaces.Add(epcWall.GetSurface(true)); / epZone.AddSurface(epcWall.GetSurface(false)); / epcWall.SetIncline(hIn, true); / Wall epfWall = walls[9] = new Wall(wl, "東室ペリメータ床"); / epfWall.SurfaceArea = 3 * 5; / outdoor.AddGroundWallSurface(epfWall.GetSurface(true)); / epZone.AddSurface(epfWall.GetSurface(false)); / Wall einWall = walls[10] = new Wall(wl, "東室インテリア北壁"); / einWall.SurfaceArea = 5 * 3; / outdoorSurfaces.Add(einWall.GetSurface(true)); / eiZone.AddSurface(einWall.GetSurface(false)); / einWall.SetIncline(nIn, true); / Wall eiwWall = walls[11] = new Wall(wl, "東室インテリア東壁"); / eiwWall.SurfaceArea = 4 * 3; / outdoorSurfaces.Add(eiwWall.GetSurface(true)); / eiZone.AddSurface(eiwWall.GetSurface(false)); / eiwWall.SetIncline(eIn, true); / Wall eicWall = walls[12] = new Wall(wl, "東室インテリア天井"); / eicWall.SurfaceArea = 4 * 5; / outdoorSurfaces.Add(eicWall.GetSurface(true)); / eiZone.AddSurface(eicWall.GetSurface(false)); / eicWall.SetIncline(hIn, true); / Wall eifWall = walls[13] = new Wall(wl, "東室インテリア床"); / eifWall.SurfaceArea = 4 * 5; / outdoor.AddGroundWallSurface(eifWall.GetSurface(true)); / eiZone.AddSurface(eifWall.GetSurface(false)); / Wall cpWall = walls[14] = new Wall(wl, "ペリメータ部の内壁"); / cpWall.SurfaceArea = 3 * 3; / wpZone.AddSurface(cpWall.GetSurface(true)); / epZone.AddSurface(cpWall.GetSurface(false)); / Wall ciWall = walls[15] = new Wall(wl, "インテリア部の内壁"); / ciWall.SurfaceArea = 4 * 3; / wiZone.AddSurface(ciWall.GetSurface(true)); / eiZone.AddSurface(ciWall.GetSurface(false)); / Wall wpsWall = walls[16] = new Wall(wl, "西側ペリメータ南壁"); / wpsWall.SurfaceArea = 5 * 3 - 3 * 2; / outdoorSurfaces.Add(wpsWall.GetSurface(true)); / wpZone.AddSurface(wpsWall.GetSurface(false)); / wpsWall.SetIncline(sIn, true); / Wall epsWall = walls[17] = new Wall(wl, "東側ペリメータ南壁"); / epsWall.SurfaceArea = 5 * 3 - 3 * 2; / outdoorSurfaces.Add(epsWall.GetSurface(true)); / epZone.AddSurface(epsWall.GetSurface(false)); / epsWall.SetIncline(sIn, true); / //外表面を初期化 / foreach (WallSurface ws in outdoorSurfaces) / { / //屋外に追加 / outdoor.AddWallSurface(ws); / //放射率を初期化 / ws.InitializeEmissivity(WallSurface.SurfaceMaterial.Concrete); / } / //窓をゾーンに追加 / Window wWind = new Window(gPanes, "西室ペリメータ南窓"); / wWind.SurfaceArea = 3 * 2; / wpZone.AddWindow(wWind); / outdoor.AddWindow(wWind); / Window eWind = new Window(gPanes, "東室ペリメータ南窓"); / eWind.SurfaceArea = 3 * 2; / eWind.Shade = SunShade.MakeHorizontalSunShade(3, 2, 1, 1, 1, 0.5, sIn); / wpZone.AddWindow(eWind); / outdoor.AddWindow(eWind); / //タイトル行書き出し / StreamWriter sWriter = new StreamWriter("室の温湿度変動テスト1.csv", false, Encoding.GetEncoding("Shift_JIS")); / foreach (Zone zn in zones) sWriter.Write(zn.Name + "乾球温度[C], " + zn.Name + / "絶対湿度[kg/kgDA], " + zn.Name + "顕熱負荷[W], " + zn.Name + "潜熱負荷[W], "); / sWriter.WriteLine(); / //計算実行 / for (int i = 0; i < 100; i++) / { / DateTime dTime = new DateTime(2007, 8, 3, 0, 0, 0); / for (int j = 0; j < 24; j++) / { / //時刻を設定 / sun.Update(dTime); / foreach (Zone zn in zones) zn.CurrentDateTime = dTime; / //空調設定 / bool operating = (8 <= dTime.Hour && dTime.Hour <= 19); / foreach (Zone zn in zones) / { / zn.ControlAbsoluteHumidity = operating; / zn.ControlDrybulbTemperature = operating; / } / //気象条件を設定 / outdoor.AirState = new MoistAir(dbt[j], ahd[j]); / outdoor.NocturnalRadiation = nrd[j]; / sun.SetGlobalHorizontalRadiation(drd[j], dnr[j]); / //換気の設定 / eiZone.VentilationAirState = new MoistAir(epZone.CurrentDrybulbTemperature, eiZone.CurrentAbsoluteHumidity); / epZone.VentilationAirState = new MoistAir(eiZone.CurrentDrybulbTemperature, eiZone.CurrentAbsoluteHumidity); / wpZone.VentilationAirState = outdoor.AirState; / wiZone.VentilationAirState = new MoistAir(wpZone.CurrentDrybulbTemperature, wpZone.CurrentAbsoluteHumidity); / //外壁表面の状態を設定 / outdoor.SetWallSurfaceBoundaryState(); / //壁体を更新 / foreach (Wall wal in walls) wal.Update(); / //ゾーンを更新 / foreach (Zone zn in zones) zn.Update(); / //時刻を更新 / dTime = dTime.AddHours(1); / //書き出し設定 / if (i == 99) / { / foreach (Zone zn in zones) / { / sWriter.Write(zn.CurrentDrybulbTemperature.ToString("F1") + ", " + zn.CurrentAbsoluteHumidity.ToString("F3") + ", " + / zn.CurrentSensibleHeatLoad.ToString("F0") + ", " + zn.CurrentLatentHeatLoad.ToString("F0") + ", "); / } / sWriter.WriteLine(); / } / } / } / sWriter.Close(); / }

図6.28　室の温湿度変動計算プログラムの例(Zoneクラスを使用する場合)
#### MultiRoomクラスを利用して解く方法

　MultiRoomクラスを利用すると複数のゾーンの温湿度を連成させて解くことができます。
　図6.22で示したとおり、本クラスライブラリでは空間をZone, Room, MultiRoomという三層の階層構造で捉えています。Zoneは対流による熱移動の範囲を表し、Roomは放射による熱移動の範囲を表します。この概念を図6.29に示します。図6.29左に示すように、あるZoneを代表する質点と、対流によって熱移動が生じる範囲はそのゾーンに属している壁や窓表面のみです。この場合ですと、質点Z1と壁窓表面W1, W2, W3との間で対流による熱移動が生じています。質点Z1と壁窓表面W4, W5, W6との間では直接的に熱の授受はありません。一方、Roomには1以上のZoneが含まれますが、図6.29右に示すとおり、同一のRoomに属する壁窓表面相互では放射による熱移動が生じるとしています。1つのRoomに壁体の両面を属させると放射による熱移動が計算できず、エラーが生じることに注意してください。

図6.29　ZoneおよびRoomクラスの意味と熱移動の範囲

　MultiRoomクラスを使用した場合の、ゾーンの顕熱平衡式を式6.23に示します。式6.18との違いは右辺第一項にあり、ゾーンに属する表面ごとに異なる表面温度と対流熱伝達率を使用しています[1]。
[1] 詳細な解法については文献2)を参照

ZN_S {d T_R} over {dt} = sum from n=1 to NW A_n %alpha_{(i)n} k_{(c)n} (T_Sn - T_R) + c_a G_o (T_a - T_R) + HG_(c) - HE_s	(6.23)

　ZNS : ゾーンの顕熱容量 [J/K],　TR : ゾーンの乾球温度 [°C],　t : 時間 [sec],　NW : ゾーンに含まれる表面の数,　An : 表面積 [m2]
　α(i) n : 表面nの総合熱伝達率 [W/(m2 K)],　k(c) n : 表面nの総合熱伝達率の対流比率 [-]
　TMRT : 周壁の平均温度 [°C],　ca : 空気の比熱 [J/(kg K)],　Go : 換気量 [kg/s],　Ta : 外気の乾球温度 [°C]
　HG(c) : 室内発生顕熱の対流成分 [W],　HEs : 室への供給熱量 [W]

　Roomクラスのコンストラクタを表6.31に示します。Roomに属するZoneオブジェクトの配列が引数です。

表6.31　Roomコンストラクタの引数一覧
No.	引数1	引数2
1	Roomに属するZone (Zone配列型)	Room名称 (string型)
2	Roomに属するZone (Zone配列型)	-

　Roomクラスのプロパティおよびメソッドを表6.32と表6.33に示します。前述したとおり、Roomクラスの主要な機能は放射による熱移動の設定にあり、プロパティおよびメソッドも放射関連の処理が中心となっています。
　放射には、窓を透過して入射する日射による短波長放射と、室内の発熱要素が発生させる長波長放射が存在します。これらの放射はRoomに属する窓や壁の表面に分配されますが、この分配比率を設定するため、SetShort(Long)WaveRadiationRateメソッドを使用します。設定を行わない場合には各表面の面積比で初期化されます。日射による短波長放射については、まずはペリメータ付近の床面に入射すると考えられますので、ペリメータ床面に大きめの比率を設定することが望ましいと考えられます。また、短波長放射の内、室内で反射を繰り返して窓表面に入射する割合は、そのまま窓を透過して室外へ出て行きます。この量はTransmissionHeatLossFromWindowで取得することができます。
　Roomに属する壁や窓表面相互の放射熱移動に関して、ある表面から別の表面への放射の比率はSetRadiativeHeatTransferRateで設定することができます。厳密には形態係数を利用した計算が必要になりますが、デフォルトでは各表面の面積を利用した式6.24で初期化されます。

%PHI_{n j} = A_j over {sum from l to NW A_l}	(6.24)

　Φn j : 表面nから表面jへの放射熱交換係数 [-],　Aj : 表面jの面積 [m2],　NW : Roomに属する表面の数 [sec]

表6.32　Roomクラスの主要なプロパティ一覧
プロパティ名称	内容	setアクセッサ	単位	型
Name	室の名称	○	-	string
SurfaceNumber	室に属する表面の数	-	-	uint
ZoneNumber	室に属するゾーンの数	-	-	uint
TransmissionHeatLossFromWindow	窓から外部への透過日射損失	-	W	double
CurrentDateTime	現在の日時	-	-	DateTime

表6.33　Roomクラスのメソッド一覧
名称	内容
SetShortWaveRadiationRate	概要	窓面の短波長放射成分入射比率[-]を設定する
	戻り値	-
	引数1	窓 (Window型)	引数2	窓面の短波長放射成分入射比率[-]
SetShortWaveRadiationRate	概要	短波長放射成分入射比率[-]を設定する
	戻り値	-
	引数1	表面 (ISurface型)	引数2	表面の短波長放射成分入射比率[-]
GetShortWaveRadiationRate	概要	窓面の短波長放射成分入射比率[-]を取得する
	戻り値	窓面の短波長放射成分入射比率[-]
	引数1	窓面 (Window型)	引数2	-
GetShortWaveRadiationRate	概要	短波長放射成分入射比率[-]を取得する
	戻り値	表面の短波長放射成分入射比率[-]
	引数1	表面 (ISurface型)	引数2	-
SetLongWaveRadiationRate	概要	窓面の長波長放射成分入射比率[-]を設定する
	戻り値	-
	引数1	窓 (Window型)	引数2	窓面の長波長放射成分入射比率[-]
SetLongWaveRadiationRate	概要	長波長放射成分入射比率[-]を設定する
	戻り値	-
	引数1	表面 (ISurface型)	引数2	表面の長波長放射成分入射比率[-]
GetLongWaveRadiationRate	概要	窓面の長波長放射成分入射比率[-]を取得する
	戻り値	窓面の長波長放射成分入射比率[-]
	引数1	窓面 (Window型)	引数2	-
GetLongWaveRadiationRate	概要	長波長放射成分入射比率[-]を取得する
	戻り値	表面の長波長放射成分入射比率[-]
	引数1	表面 (ISurface型)	引数2	-
SetRadiativeHeatTransferRate	概要	表面1から表面2への放射熱交換係数[-]を設定する
	戻り値	表面1から表面2への放射熱交換係数[-]
	引数1	表面1 (ISurface型)	引数2	表面2 (ISurface型)
GetRadiativeHeatTransferRate	概要	表面1から表面2への放射熱交換係数[-]を取得する
	戻り値	表面1から表面2への放射熱交換係数[-]
	引数1	表面1 (ISurface型)	引数2	表面2 (ISurface型)

　MultiRoomクラスのコンストラクタは、下記に示すように、引数としてRoom型配列をとります。

MultiRoom mRoom = new MultiRoom(rooms);

　MultiRoomクラスの主要なメソッドを表6.34に示します。SetAirFlowを使用することでRoomをまたいで室間換気量を設定することができます。各室の状態を更新するためにはUpdateRoomTemperaturesおよびUpdateRoomHumiditiesを使用します。

表6.34　MultiRoomクラスのメソッド一覧
名称	内容
UpdateRoomTemperatures	概要	室の乾球温度を更新する
	戻り値	-
	引数1	-	引数2	-
UpdateRoomHumidities	概要	室の絶対湿度を更新する
	戻り値	-
	引数1	-	引数2	-
SetTimeStep	概要	計算時間間隔[s]を設定する
	戻り値	-
	引数1	計算時間間隔[s]	引数2	-
SetAirFlow	概要	室間換気量[m3/h]を設定する
	戻り値	-
	引数1	上流（空気が吹き出す側）の室	引数2	下流（空気が吹き込む側）の室
	引数3	室間換気量[m3/h]	引数4	-
GetAirFlow	概要	室間換気量[m3/h]を取得する
	戻り値	室間換気量[m3/h]
	引数1	上流（空気が吹き出す側）の室	引数2	下流（空気が吹き込む側）の室
SetCurrentDateTime	概要	現在の日時を設定する
	戻り値	-
	引数1	現在の日時 (DateTime型)	引数2	-

　MultiRoomクラスを使用して1)で説明した多数室の計算を行うプログラムの例を図6.30に示します。多くの行は、図6.28に示したZoneを使用するプログラムと同じですが、一部、異なるところがあります。
　179~183行でRoomオブジェクトおよびMultiRoomオブジェクトを作成しています。西室のペリメータ部およびインテリア部を合わせて西Room、東室のペリメータ部およびインテリア部を合わせて東Roomとしています。
　185~189行では室間換気量を設定しています。西室ペリメータ部についてのみ外気導入を設定していることに注意して下さい。
　191~201行では短波長放射の入射比率を設定しており、ペリメータ床の比率を0.6、その他の表面については面積比率としています。
　定常状態になるように同一気象データで100回の繰り返し計算を行い、100回目に書き出しを行っています。

1 / 2 / 3 / 4 / 5 / 6 / 7 / 8 / 9 / 10 / 11 / 12 / 13 / 14 / 15 / 16 / 17 / 18 / 19 / 20 / 21 / 22 / 23 / 24 / 25 / 26 / 27 / 28 / 29 / 30 / 31 / 32 / 33 / 34 / 35 / 36 / 37 / 38 / 39 / 40 / 41 / 42 / 43 / 44 / 45 / 46 / 47 / 48 / 49 / 50 / 51 / 52 / 53 / 54 / 55 / 56 / 57 / 58 / 59 / 60 / 61 / 62 / 63 / 64 / 65 / 66 / 67 / 68 / 69 / 70 / 71 / 72 / 73 / 74 / 75 / 76 / 77 / 78 / 79 / 80 / 81 / 82 / 83 / 84 / 85 / 86 / 87 / 88 / 89 / 90 / 91 / 92 / 93 / 94 / 95 / 96 / 97 / 98 / 99 / 100 / 101 / 102 / 103 / 104 / 105 / 106 / 107 / 108 / 109 / 110 / 111 / 112 / 113 / 114 / 115 / 116 / 117 / 118 / 119 / 120 / 121 / 122 / 123 / 124 / 125 / 126 / 127 / 128 / 129 / 130 / 131 / 132 / 133 / 134 / 135 / 136 / 137 / 138 / 139 / 140 / 141 / 142 / 143 / 144 / 145 / 146 / 147 / 148 / 149 / 150 / 151 / 152 / 153 / 154 / 155 / 156 / 157 / 158 / 159 / 160 / 161 / 162 / 163 / 164 / 165 / 166 / 167 / 168 / 169 / 170 / 171 / 172 / 173 / 174 / 175 / 176 / 177 / 178 / 179 / 180 / 181 / 182 / 183 / 184 / 185 / 186 / 187 / 188 / 189 / 190 / 191 / 192 / 193 / 194 / 195 / 196 / 197 / 198 / 199 / 200 / 201 / 202 / 203 / 204 / 205 / 206 / 207 / 208 / 209 / 210 / 211 / 212 / 213 / 214 / 215 / 216 / 217 / 218 / 219 / 220 / 221 / 222 / 223 / 224 / 225 / 226 / 227 / 228 / 229 / 230 / 231 / 232 / 233 / 234 / 235 / 236 / 237 / 238 / 239 / 240 / 241 / 242 / 243 / 244 / 245 / 246 / 247 / 248 / 249 / 250 / 251 / 252 / 253 / 254 / 255 / 256 / 257 / 258 / 259 / 260 / 261 / 262 / 263	/// <summary>室の温湿度変動テスト(MultiRoomクラス)</summary> / private static void RoomModelTest2() / { / //気象データ:乾球温度,絶対湿度,夜間放射,直達日射,天空日射 / double[] dbt = new double[] { 24.2, 24.1, 24.1, 24.2, 24.3, 24.2, 24.4, 25.1, 26.1, 27.1, 28.8, 29.9, / 30.7, 31.2, 31.6, 31.4, 31.3, 30.8, 29.4, 28.1, 27.5, 27.1, 26.6, 26.3 }; / double[] ahd = new double[] { 0.0134, 0.0136, 0.0134, 0.0133, 0.0131, 0.0134, 0.0138, 0.0142, 0.0142, 0.0140, 0.0147, 0.0149, / 0.0142, 0.0146, 0.0140, 0.0145, 0.0144, 0.0146, 0.0142, 0.0136, 0.0136, 0.0135, 0.0136, 0.0140 }; / double[] nrd = new double[] { 32, 30, 30, 29, 26, 24, 24, 25, 25, 25, 24, 24, 24, 23, 24, 24, 24, 24, 23, 23, 24, 26, 25, 23 }; / double[] dnr = new double[] { 0, 0, 0, 0, 0, 0, 106, 185, 202, 369, 427, 499, 557, 522, 517, 480, 398, 255, 142, 2, 0, 0, 0, 0 }; / double[] drd = new double[] { 0, 0, 0, 0, 0, 0, 36, 115, 198, 259, 314, 340, 340, 349, 319, 277, 228, 167, 87, 16, 0, 0, 0, 0 }; / //屋外を作成 / Outdoor outdoor = new Outdoor(); / Sun sun = new Sun(Sun.City.Tokyo); / outdoor.Sun = sun; / outdoor.GroundTemperature = 25; / //傾斜を作成 / Incline nIn = new Incline(Incline.Orientation.N, 0.5 * Math.PI); //北 / Incline eIn = new Incline(Incline.Orientation.E, 0.5 * Math.PI); //東 / Incline wIn = new Incline(Incline.Orientation.W, 0.5 * Math.PI); //西 / Incline sIn = new Incline(Incline.Orientation.S, 0.5 * Math.PI); //南 / Incline hIn = new Incline(Incline.Orientation.S, 0); //水平 / //ゾーンを作成 / Zone[] zones = new Zone[4]; / Zone wpZone = zones[0] = new Zone("西室ペリメータ"); / wpZone.Volume = 3 * 5 * 3; / Zone wiZone = zones[1] = new Zone("西室インテリア"); / wiZone.Volume = 4 * 5 * 3; / Zone epZone = zones[2] = new Zone("東室ペリメータ"); / epZone.Volume = 3 * 5 * 3; / Zone eiZone = zones[3] = new Zone("東室インテリア"); / eiZone.Volume = 4 * 5 * 3; / foreach (Zone zn in zones) / { / zn.TimeStep = 3600; / zn.DrybulbTemperatureSetPoint = 26; / zn.AbsoluteHumiditySetPoint = 0.01; / } / //東側インテリアに発熱体を設定 / eiZone.AddHeatGain(new ConstantHeatGain(100, 100, 20)); / //壁構成を作成:400mmコンクリート / WallLayers wl = new WallLayers(); / wl.AddLayer(new WallLayers.Layer(new WallMaterial(WallMaterial.PredefinedMaterials.ReinforcedConcrete), 0.4)); / //窓構成を作成 / GlassPanes gPanes = new GlassPanes(new GlassPanes.Pane(GlassPanes.Pane.PredifinedGlassPane.HeatReflectingGlass06mm)); / //壁体をゾーンに追加 / Wall[] walls = new Wall[18]; / List<WallSurface> outdoorSurfaces = new List<WallSurface>(); / Wall wpwWall = walls[0] = new Wall(wl, "西室ペリメータ西壁"); / wpwWall.SurfaceArea = 3 * 3; / outdoorSurfaces.Add(wpwWall.GetSurface(true)); / wpZone.AddSurface(wpwWall.GetSurface(false)); / wpwWall.SetIncline(wIn, true); / Wall wpcWall = walls[1] = new Wall(wl, "西室ペリメータ天井"); / wpcWall.SurfaceArea = 3 * 5; / outdoorSurfaces.Add(wpcWall.GetSurface(true)); / wpZone.AddSurface(wpcWall.GetSurface(false)); / wpcWall.SetIncline(hIn, true); / Wall wpfWall = walls[2] = new Wall(wl, "西室ペリメータ床"); / wpfWall.SurfaceArea = 3 * 5; / outdoor.AddGroundWallSurface(wpfWall.GetSurface(true)); / wpZone.AddSurface(wpfWall.GetSurface(false)); / Wall winWall = walls[3] = new Wall(wl, "西室インテリア北壁"); / winWall.SurfaceArea = 3 * 5; / outdoorSurfaces.Add(winWall.GetSurface(true)); / wiZone.AddSurface(winWall.GetSurface(false)); / winWall.SetIncline(nIn, true); / Wall wiwWall = walls[4] = new Wall(wl, "西室インテリア西壁"); / wiwWall.SurfaceArea = 3 * 4; / outdoorSurfaces.Add(wiwWall.GetSurface(true)); / wiZone.AddSurface(wiwWall.GetSurface(false)); / wiwWall.SetIncline(wIn, true); / Wall wicWall = walls[5] = new Wall(wl, "西室インテリア天井"); / wicWall.SurfaceArea = 4 * 5; / outdoorSurfaces.Add(wicWall.GetSurface(true)); / wiZone.AddSurface(wicWall.GetSurface(false)); / wicWall.SetIncline(hIn, true); / Wall wifWall = walls[6] = new Wall(wl, "西室インテリア床"); / wifWall.SurfaceArea = 4 * 5; / outdoor.AddGroundWallSurface(wifWall.GetSurface(true)); / wiZone.AddSurface(wifWall.GetSurface(false)); / Wall epwWall = walls[7] = new Wall(wl, "東室ペリメータ東壁"); / epwWall.SurfaceArea = 3 * 3; / outdoorSurfaces.Add(epwWall.GetSurface(true)); / epZone.AddSurface(epwWall.GetSurface(false)); / epwWall.SetIncline(eIn, true); / Wall epcWall = walls[8] = new Wall(wl, "東室ペリメータ天井"); / epcWall.SurfaceArea = 3 * 5; / outdoorSurfaces.Add(epcWall.GetSurface(true)); / epZone.AddSurface(epcWall.GetSurface(false)); / epcWall.SetIncline(hIn, true); / Wall epfWall = walls[9] = new Wall(wl, "東室ペリメータ床"); / epfWall.SurfaceArea = 3 * 5; / outdoor.AddGroundWallSurface(epfWall.GetSurface(true)); / epZone.AddSurface(epfWall.GetSurface(false)); / Wall einWall = walls[10] = new Wall(wl, "東室インテリア北壁"); / einWall.SurfaceArea = 5 * 3; / outdoorSurfaces.Add(einWall.GetSurface(true)); / eiZone.AddSurface(einWall.GetSurface(false)); / einWall.SetIncline(nIn, true); / Wall eiwWall = walls[11] = new Wall(wl, "東室インテリア東壁"); / eiwWall.SurfaceArea = 4 * 3; / outdoorSurfaces.Add(eiwWall.GetSurface(true)); / eiZone.AddSurface(eiwWall.GetSurface(false)); / eiwWall.SetIncline(eIn, true); / Wall eicWall = walls[12] = new Wall(wl, "東室インテリア天井"); / eicWall.SurfaceArea = 4 * 5; / outdoorSurfaces.Add(eicWall.GetSurface(true)); / eiZone.AddSurface(eicWall.GetSurface(false)); / eicWall.SetIncline(hIn, true); / Wall eifWall = walls[13] = new Wall(wl, "東室インテリア床"); / eifWall.SurfaceArea = 4 * 5; / outdoor.AddGroundWallSurface(eifWall.GetSurface(true)); / eiZone.AddSurface(eifWall.GetSurface(false)); / Wall cpWall = walls[14] = new Wall(wl, "ペリメータ部の内壁"); / cpWall.SurfaceArea = 3 * 3; / wpZone.AddSurface(cpWall.GetSurface(true)); / epZone.AddSurface(cpWall.GetSurface(false)); / Wall ciWall = walls[15] = new Wall(wl, "インテリア部の内壁"); / ciWall.SurfaceArea = 4 * 3; / wiZone.AddSurface(ciWall.GetSurface(true)); / eiZone.AddSurface(ciWall.GetSurface(false)); / Wall wpsWall = walls[16] = new Wall(wl, "西側ペリメータ南壁"); / wpsWall.SurfaceArea = 5 * 3 - 3 * 2; / outdoorSurfaces.Add(wpsWall.GetSurface(true)); / wpZone.AddSurface(wpsWall.GetSurface(false)); / wpsWall.SetIncline(sIn, true); / Wall epsWall = walls[17] = new Wall(wl, "東側ペリメータ南壁"); / epsWall.SurfaceArea = 5 * 3 - 3 * 2; / outdoorSurfaces.Add(epsWall.GetSurface(true)); / epZone.AddSurface(epsWall.GetSurface(false)); / epsWall.SetIncline(sIn, true); / //外表面を初期化 / foreach (WallSurface ws in outdoorSurfaces) / { / //屋外に追加 / outdoor.AddWallSurface(ws); / //放射率を初期化 / ws.InitializeEmissivity(WallSurface.SurfaceMaterial.Concrete); / } / //窓をゾーンに追加 / Window wWind = new Window(gPanes, "西室ペリメータ南窓"); / wWind.SurfaceArea = 3 * 2; / wpZone.AddWindow(wWind); / outdoor.AddWindow(wWind); / Window eWind = new Window(gPanes, "東室ペリメータ南窓"); / eWind.SurfaceArea = 3 * 2; / eWind.Shade = SunShade.MakeHorizontalSunShade(3, 2, 1, 1, 1, 0.5, sIn); / wpZone.AddWindow(eWind); / outdoor.AddWindow(eWind); / //多数室オブジェクトを作成 / Room eRm = new Room(new Zone[] { epZone, eiZone }); //東側の室 / Room wRm = new Room(new Zone[] { wpZone, wiZone }); //西側の室 / MultiRoom mRoom = new MultiRoom(new Room[] { eRm, wRm }); //多数室 / mRoom.SetTimeStep(3600); / //換気の設定 / wpZone.VentilationVolume = 10; //西室ペリメータのみ外気導入 / mRoom.SetAirFlow(wpZone, wiZone, 10); / mRoom.SetAirFlow(epZone, eiZone, 10); / mRoom.SetAirFlow(eiZone, epZone, 10); / //短波長放射の入射比率を調整:ペリメータ床面6割、その他は面積比率 / double sfSum = 0; / foreach (ISurface isf in eRm.GetSurface()) sfSum += isf.Area; / sfSum -= epfWall.SurfaceArea; / foreach (ISurface isf in eRm.GetSurface()) eRm.SetShortWaveRadiationRate(isf, isf.Area / sfSum * 0.4); / eRm.SetShortWaveRadiationRate(epfWall.GetSurface(false), 0.6); / sfSum = 0; / foreach (ISurface isf in wRm.GetSurface()) sfSum += isf.Area; / sfSum -= wpfWall.SurfaceArea; / foreach (ISurface isf in wRm.GetSurface()) wRm.SetShortWaveRadiationRate(isf, isf.Area / sfSum * 0.4); / wRm.SetShortWaveRadiationRate(wpfWall.GetSurface(false), 0.6); / //タイトル行書き出し / StreamWriter sWriter = new StreamWriter("室の温湿度変動テスト2.csv", false, Encoding.GetEncoding("Shift_JIS")); / foreach (Zone zn in zones) sWriter.Write(zn.Name + "乾球温度[C], " + zn.Name + "絶対湿度[kg/kgDA], " / + zn.Name + "顕熱負荷[W], " + zn.Name + "潜熱負荷[W], "); / sWriter.WriteLine(); / //計算実行 / for (int i = 0; i < 100; i++) / { / DateTime dTime = new DateTime(2007, 8, 3, 0, 0, 0); / for (int j = 0; j < 24; j++) / { / //時刻を設定 / sun.Update(dTime); / mRoom.SetCurrentDateTime(dTime); / //空調設定 / bool operating = (8 <= dTime.Hour && dTime.Hour <= 19); / foreach (Zone zn in zones) / { / zn.ControlAbsoluteHumidity = operating; / zn.ControlDrybulbTemperature = operating; / } / //気象条件を設定 / outdoor.AirState = new MoistAir(dbt[j], ahd[j]); / outdoor.NocturnalRadiation = nrd[j]; / sun.SetGlobalHorizontalRadiation(drd[j], dnr[j]); / //換気の設定 / wpZone.VentilationAirState = outdoor.AirState; / //外壁表面の状態を設定 / outdoor.SetWallSurfaceBoundaryState(); / //壁体を更新 / foreach (Wall wal in walls) wal.Update(); / //多数室を更新 / mRoom.UpdateRoomTemperatures(); / mRoom.UpdateRoomHumidities(); / //時刻を更新 / dTime = dTime.AddHours(1); / //書き出し設定 / if (i == 99) / { / foreach (Zone zn in zones) / { / sWriter.Write(zn.CurrentDrybulbTemperature.ToString("F1") + ", " + zn.CurrentAbsoluteHumidity.ToString("F3") + ", " + / zn.CurrentSensibleHeatLoad.ToString("F0") + ", " + zn.CurrentLatentHeatLoad.ToString("F0") + ", "); / } / sWriter.WriteLine(); / } / } / } / sWriter.Close(); / }

図6.30　室の温湿度変動計算プログラムの例(MultiRoomクラスを使用する場合)

　図6.31と図6.32に計算結果を示します。MultiRoomでは室間換気を考慮した連成計算を行っているため、西側ペリメータで導入した外気の影響がインテリア部にも表れており、Zoneクラスのみを使用した場合の図6.27と比較すると、インテリア部の熱負荷が上昇していることがわかります。

図6.31　乾球温度の推移

図6.32　顕熱負荷の推移